## Step 1 - Load Sizing
[7 empty] | Calculated |  | Only use this section to manually input loading for each home. Manual load values will override the calculated values ot the left.
|  |  | Base | AC | Cooling | Heat | Summer | Winter
|  |  | Load | Size | Load | Load | Load | Load |  | Summer Load |  | Winter Load
Home | Home Square Footage |  | kVA | Tons | kVA | kVA | kVA | kVA |  |  | kVA |  | kVA
A |  | 0 | [6 empty] | Enter a value for Square footage to activate User Input for Summer and Winter Loads |  | 0 |  | 0 | 0 |  | 0 | 0 | FALSE | FALSE
B |  | 0 | [8 empty] | 0 |  | 0 | 0 | FALSE |  |  | FALSE | FALSE
C |  | 0 | [8 empty] | 0 |  | 0 |  |  |  |  | FALSE | FALSE
D |  | 0 | [8 empty] | 0 |  | 0 |  |  |  |  | FALSE | FALSE
E |  | 0 | [8 empty] | 0 |  | 0 |  |  |  |  | FALSE | FALSE
F |  | 0 | [8 empty] | 0 |  | 0 |  |  |  |  | FALSE | FALSE
G |  | 0 | [8 empty] | 0 |  | 0 |  |  |  |  | FALSE | FALSE
H |  | 0 | [8 empty] | 0 |  | 0 |  |  |  |  | FALSE | FALSE
I |  | 0 | [8 empty] | 0 |  | 0 |  |  |  |  | FALSE | FALSE
J |  | 0 | [8 empty] | 0 |  | 0 |  |  |  |  | FALSE | FALSE
| Instructions: | [14 empty] | 0
1. Add individual homes by using the arrows to the left to adjust square footage of each home.
2. Appropriate AC size and summer and winter loading will be automatically calculated
3. (Optional) If a home uses electric heat in the winter, check the "Electric Heat" box. Loads will be updated to reflect the change.
4. (Optional) If any home has a loading different from the calculated value, use the box to the right to manually enter a load.
5. Once you are satisfied with your inputs, please continue to Step 2 - Transformer Sizing
[15 empty] | Tons | Cooling | Heating
[14 empty] | 100 | 1 | 2 | 5
[14 empty] | 200 | 1 | 2 | 5
[14 empty] | 300 | 1 | 2 | 5
[14 empty] | 400 | 1 | 2 | 5
[14 empty] | 500 | 1 | 2 | 5
[14 empty] | 600 | 1.5 | 3 | 5
[14 empty] | 700 | 1.5 | 3 | 5
[14 empty] | 800 | 1.5 | 3 | 5
[14 empty] | 900 | 1.5 | 3 | 5
[14 empty] | 1000 | 2 | 4 | 6
[14 empty] | 1100 | 2 | 4 | 6
[14 empty] | 1200 | 2 | 4 | 6
[14 empty] | 1300 | 2.5 | 5 | 8
[14 empty] | 1400 | 2.5 | 5 | 8
[14 empty] | 1500 | 2.5 | 5 | 8
[14 empty] | 1600 | 3 | 5.5 | 9
[14 empty] | 1700 | 3 | 5.5 | 9
[14 empty] | 1800 | 3 | 5.5 | 9
[14 empty] | 1900 | 3.5 | 7 | 10.5
[14 empty] | 2000 | 3.5 | 7 | 10.5
[14 empty] | 2100 | 3.5 | 7 | 10.5
[14 empty] | 2200 | 4 | 8 | 12.5
[14 empty] | 2300 | 4 | 8 | 12.5
[14 empty] | 2400 | 4 | 8 | 12.5
[14 empty] | 2500 | 5 | 10 | 16
[14 empty] | 2600 | 5 | 10 | 16
[14 empty] | 2700 | 5 | 10 | 16
[14 empty] | 2800 | 5 | 10 | 16
[14 empty] | 2900 | 5 | 10 | 16
[14 empty] | 3000 | 5 | 10 | 16
[12 empty] | 2x Unit |  | 3100 | 3 | 5.5 | 9
[12 empty] | 2x Unit |  | 3200 | 3 | 5.5 | 9
[12 empty] | 2x Unit |  | 3300 | 3 | 5.5 | 9
[12 empty] | 2x Unit |  | 3400 | 3 | 5.5 | 9
[12 empty] | 2x Unit |  | 3500 | 3 | 5.5 | 9
[12 empty] | 2x Unit |  | 3600 | 3 | 5.5 | 9
[12 empty] | 2x Unit |  | 3700 | 3.5 | 7 | 10.5
[12 empty] | 2x Unit |  | 3800 | 3.5 | 7 | 10.5
[12 empty] | 2x Unit |  | 3900 | 3.5 | 7 | 10.5
[12 empty] | 2x Unit |  | 4000 | 3.5 | 7 | 10.5
[12 empty] | 2x Unit |  | 4100 | 3.5 | 7 | 10.5
[12 empty] | 2x Unit |  | 4200 | 3.5 | 7 | 10.5
[12 empty] | 2x Unit |  | 4300 | 4 | 8 | 12.5
[12 empty] | 2x Unit |  | 4400 | 4 | 8 | 12.5
[12 empty] | 2x Unit |  | 4500 | 4 | 8 | 12.5
[12 empty] | 2x Unit |  | 4600 | 4 | 8 | 12.5
[12 empty] | 2x Unit |  | 4700 | 4 | 8 | 12.5
[12 empty] | 2x Unit |  | 4800 | 4 | 8 | 12.5
[12 empty] | 2x Unit |  | 4900 | 5 | 10 | 16
[12 empty] | 2x Unit |  | 5000 | 5 | 10 | 16
Electric Heat
Electric Heat
Electric Heat
Electric Heat
Electric Heat
Electric Heat
Electric Heat
Electric Heat
Electric Heat
Electric Heat
LOAD SIZING WORKSHEET

## Step 2 - Transformer Sizing
[7 empty] | Transformer kVA | [7 empty] | kV | 0.24
|  | Impedance Values |  |  |  |  | 10 | 15 | 25 | 37.5 | 50 | 75 | 100 | 167
Transformer Size: | 10 | Z% | 2.0963 | X/R Ratio | 0.5 | RT | 0.108 | 0.064 | 0.031 | 0.019 | 0.011 | 0.007 | 0.005 | 0.003 | Pulled from "Voltage Drop Table" Equations
|  | RT | 0.108 | XT | 0.054 | XT | 0.054 | 0.035 | 0.028 | 0.02 | 0.016 | 0.01 | 0.009 | 0.006 | ^^^These values are hard-coded into the calculations on that page.
|  | Full-Load Losses (W) |  | 187.5 |  | ZT | 0.12075 | 0.072945 | 0.041773 | 0.027586 | 0.019416 | 0.012207 | 0.010296 | 0.0067082 | Transformer Size |  | 1 | 10
[6 empty] | R% | 1.875 | 1.6667 | 1.3455 | 1.237 | 0.95486 | 0.91146 | 0.86806 | 0.86979
If you would like to use different impedance values, select the box next to "USER INPUT." Otherwise, please continue to Step 3 - Calculator | [5 empty] | X% | 0.9375 | 0.91146 | 1.2153 | 1.3021 | 1.3889 | 1.3021 | 1.5625 | 1.7396
[6 empty] | Z% | 2.0963 | 1.8996 | 1.8131 | 1.796 | 1.6855 | 1.5894 | 1.7874 | 1.9449
[6 empty] | Rated Losses | 187.5 | 250 | 336.3715 | 463.8672 | 477.4306 | 683.5938 | 868.0556 | 1452.5521
USER INPUT |  | Resulting Impedance Values |  |  |  | User Input |  | FALSE
Z% |  | Z% |  | X/R Ratio |  | Calculation of X, R using Z% and Losses
Full-Load Loss (W) |  | RT |  | XT |  | Z% |  | 0
|  | Full-Load Losses (W) |  |  |  | Rated Load Loss (W) |  | 0
[6 empty] | R% | 0 |  | RT | 0
[6 empty] | X% | 0 |  | XT | 0
TRANSFORMER SIZING WORKSHEET

## Step 3 - Calculator
Transformer Sizing, Voltage Drop, and Voltage Flicker Analysis Developed by Hi-Line Engineering, a GDS Company
Transromer Calculations
Home Size
Sec. Wire Selection
| Be sure to complete Step 1 and Step 2 before calculating Voltage Drop and Voltage Flicker |  |  |  |  | Homes |  | Summer | Winter | Homes | Homes | Home | [26 empty] | 120
[6 empty] | Served | Square | Load | Load | Served by | Served by | Served by | [9 empty] | Transformer |  | Pedestal
[6 empty] | by Transf. | Feet | kVA | kVA | Transformer | Secondary | Service | [6 empty] | 0 | 0 |  | Summer | Winter | Summer | Winter
[6 empty] | A | 0 | [9 empty] | 1 | A | FALSE | FALSE | 1 |  |  |  |  | 0 | 0 | No Transf | 0 | 0
[6 empty] | B | 0 | [9 empty] | 2 | B | FALSE | [6 empty] | 0 |  |  | 0 | 1
[6 empty] | C | 0 | [9 empty] | 3 | C | [7 empty] | 0 |  |  | 0 | 2
[6 empty] | D | 0 | [9 empty] | 4 | D | [7 empty] | 0 |  |  | 0 | 2 | [8 empty] | Serv. Wire Selection
[6 empty] | E | 0 | [9 empty] | 5 | E | [7 empty] | 0 |  |  | 0 | 0 | [8 empty] | 130
Service Lines | [5 empty] | F | 0 | [9 empty] | 6 | F | [7 empty] | 0 |  |  | 0 | 0
[6 empty] | G | 0 | [9 empty] | 7 | G | [7 empty] | 0 |  |  | 0 | 0
[6 empty] | H | 0 | [9 empty] | 8 | H | [7 empty] | 0 |  |  | 0 | 0
| Transformer | Secondary Line |  |  |  | I | 0 | [9 empty] | 9 | I | [7 empty] | 0 |  |  | 0 | 0 | [8 empty] | Serv. Selection
[6 empty] | J | 0 | [9 empty] | 10 | J | [7 empty] | 0 |  |  | 0 | 50 | [8 empty] | 0
[7 empty] | Manually-Entered Load Values | [13 empty] | Total | 0 | 0 | 0 | 0
|  |  | Please select homes connected to transformer above | [17 empty] | Diversfied Total
[22 empty] | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  |  |  | A/C (1=Yes, 2=No)
[14 empty] | 1 | [6 empty] | Suggested Transf | N/A | N/A
| TRANSFORMER Voltage Drop |  |  |  | Use Check Box to Select Homes Served by Transformer |  |  | TRANSFORMER Voltage Flicker | [13 empty] | 0 | [7 empty] | Electric Heat (1=Yes, 2=No) | [6 empty] | AC Options |  | AC Selection
|  |  | Summer | Winter | [32 empty] | 1 | 1 |  | #N/A
| Number of Homes ServedXFMR = | [6 empty] | A/C Size (Tons) = |  |  |  | Home A Selected | [7 empty] | FALSE | [6 empty] | Xfmr Options |  |  |  | Xfmr Choice | [5 empty] | 1.5 | 2
| Transformer Size (kVA) = |  | 10 | 10 |  |  |  | Transformer Size (kVA) = |  |  | 10 | [8 empty] | FALSE | [6 empty] | 1 | 10 | 1 | [7 empty] | 2 | 3
| Load (kVA) = |  | #VALUE! | #VALUE! |  |  |  | Lock Rotor Amps (LRA) = | [11 empty] | FALSE | [6 empty] | 2 | 15 | 10 | [7 empty] | 2.5 | 4
| Voltage DropXFMR (%) = | [6 empty] | Voltage FlickerXFMR (%) = | [11 empty] | FALSE | [6 empty] | 3 | 25 | [8 empty] | 3 | 5
[27 empty] | 4 | 37.5 | [8 empty] | 3.5 | 6
| SECONDARY Voltage Drop | [6 empty] | SECONDARY Voltage Flicker | [18 empty] | 5 | 50 | [8 empty] | 4 | 7
|  |  | Summer | Winter | [22 empty] | 6 | 75 | [8 empty] | 5 | 8
| Number of Homes ServedSEC = |  |  |  | Service is not connected to the Secondary |  |  | Lock Rotor Amps (LRA) = | [18 empty] | 7 | 100 | [8 empty] | Xfmr Options |  | Xfmr Seclection
| Type of WireSEC = |  |  | 4/0 TPX |  |  |  | Type of WireSEC = |  |  | 4/0 TPX | [15 empty] | 8 | 167 | # Homes Served |  | # Homes on Xfmr | Xfmr Rounded Load |  |  |  |  | 10 | 1 | 10 | 1
| LengthSEC (ft.) = |  | 120 | 120 |  |  |  | LengthSEC (ft.) = |  |  | 120 | [18 empty] | 1 | 4 | #VALUE! | (use this number to search in voltage drop table, should I be doing this?) |  |  |  | 15 | 2
| Load (kVA) = |  | #VALUE! | #VALUE! |  |  |  | Voltage Flicker100 (%) = | [21 empty] | 2 | [6 empty] | 25 | 3
| Voltage Drop100 (%) = | [6 empty] | Voltage FlickerSEC (%) = | [21 empty] | 3 | [6 empty] | 37.5 | 4
| Voltage DropSEC (%) = | [28 empty] | 4 | [6 empty] | 50 | 5
[30 empty] | 5 | [6 empty] | 75 | 6
[30 empty] | 6 | [6 empty] | 100 | 7
[30 empty] | 7 | [6 empty] | 167 | 8
| SERVICE Voltage Drop | [6 empty] | SERVICE Voltage Flicker | [21 empty] | 8 | [6 empty] | Sec Options |  | Sec. Seclection
|  |  | Summer | Winter | [24 empty] | Wire Options |  |  | # Homes on Sec |  | Sec Rounded Load | Secondary Home Serrved |  | 4 TPX | 1 | 4/0 TPX | 4
| Home ServedSERV = |  | A | A |  |  |  | Lock Rotor Amps (LRA) = | [20 empty] | 1 | 4 TPX | 4 | 2 |  | #VALUE! |  |  | 2 TPX | 2
| Type of WireSERV = |  |  | 1/0 TPX |  |  |  | Type of WireSERV = |  |  | 1/0 TPX | [17 empty] | 2 | 2 TPX |  | 2 |  |  | 1 | 1 | 1/0 TPX | 3
| LengthSERV (ft.) = |  | 130 | 130 |  |  |  | LengthSERV (ft.) = |  |  | 130 | [17 empty] | 3 | 1/0 TPX |  |  |  |  | 2 | 2 | 4/0 TPX | 4
| Load (kVA)= |  | #VALUE! | #VALUE! |  |  |  | Voltage Flicker100 (%) = | [20 empty] | 4 | 4/0 TPX |  |  |  |  | 3 | 3 | 2/0 URD | 5
| Voltage Drop100 (%) = | [6 empty] | Voltage FlickerSERV (%) = | [20 empty] | 5 | 2/0 URD | 120 |  |  |  | 4 | 4 | 4/0 URD | 6
| Voltage DropSERV (%) = | [27 empty] | 6 | 4/0 URD |  |  |  |  | N/A | N/A | 350 URD | 7
[29 empty] | 7 | 350 URD |  | # Homes on Serv |  | Serv Rounded Load | N/A | N/A | 500 URD | 8
[29 empty] | 8 | 500 URD | 3 |  |  | #VALUE! | N/A | N/A | Serv Options |  | Service. Seclection
[15 empty] | Summer VD | Winter VD | Flicker | [14 empty] | 1 |  |  | N/A | N/A | 4 TPX | 1 | 1/0 TPX | 3
|  | Calculator Results | [10 empty] | Calculator Results | [17 empty] | 130 | 1 |  |  | 0 | 0 | 2 TPX | 2
[13 empty] | Transformer | [23 empty] | 1/0 TPX | 3
[13 empty] | Secondary Conductor | [23 empty] | 4/0 TPX | 4
|  | Contributor |  | Summer Voltage Drop (%) |  | Winter Voltage Drop (%) |  | Voltage Flicker (%) |  |  |  |  | Service Conductor | [23 empty] | 2/0 URD | 5
[37 empty] | 4/0 URD | 6
|  | Transformer | [34 empty] | 350 URD | 7
[37 empty] | 500 URD | 8
Secondary Conductor
Service Conductor
Total
VDTOT(%) = VDXFMR(%) + VDSEC(%) + VDSERV(%) GOAL TO BE LESS THAN 3.33% VFTOT(%) = VFXFMR(%) + VFSEC(%) +VFSERV(%) GOAL TO BE LESS THAN 4.00%
TRANSFORMER Voltage Drop
Transformer Size (kVA) = | [26 empty] | Xfmr Options |  |  |  | Xfmr Choice
Number of Homes ServedXFMR = | [27 empty] | 10
Load (kVA) = | [27 empty] | 15
Voltage DropXFMR (%) = | [27 empty] | 25
[6 empty] | SECONDARY Voltage Drop | [21 empty] | 37.5
50
SERVICE Voltage Drop | [27 empty] | 75
[6 empty] | MAX Voltage DropSEC (%) = | [21 empty] | 100
Number of Homes ServedSERV = | [27 empty] | 167 | # Homes Served |  | # Homes on Xfmr | Xfmr Rounded Load
Type of WireSERV = | [5 empty] | Number of Homes ServedSEC = | [23 empty] | 1 |  | #VALUE! | (use this number to search in voltage drop table, should I be doing this?)
LengthSEC (ft.) = | [29 empty] | 2
Load (kVA) = | [5 empty] | Type of WireSERV = | [23 empty] | 3
Voltage Drop100 (%) = | [29 empty] | 4
Voltage DropSERV (%) = | [5 empty] | Load (kVA)= | [23 empty] | 5
6
[6 empty] | Voltage Drop100 (%) = | [23 empty] | 7
8
[6 empty] | MAX LengthSEC (ft.) = | [22 empty] | Wire Options |  | Sec Wire Choice | # Homes on Sec |  | Sec Rounded Load
TOTAL Voltage Drop | [29 empty] | 1/0 URD |  |  |  | #VALUE!
2/0 URD
Voltage DropTOT (%) = |  |  | 3.33 | [26 empty] | 4/0 URD
Voltage DropSERV (%) = | [29 empty] | 350 URD | Length of Sec.
Voltage DropXFMR (%) = | [29 empty] | 500 URD
MAX Voltage DropSEC (%) =
MAX VDSEC = VDTOT - (VDXFMR + VDSERV) | [30 empty] | Serv. Wire Choice | # Homes on Serv |  | Serv Rounded Load
#VALUE!
Length of Serv.
TRUE
VOLTAGE DROP and VOLTAGE FLICKER WORKSHEET

## Transf Sizing Data (hidden)
Transformer Sizing Utility developed solely by HiLine Engineering, LLC
[12 empty] | 1 | 0 | 1
Guide for Estimating Load on Transformer Based on Number of Residential Homes
BASE LOAD IN kVA
Number of Homes
| Home Size |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
| Less Than 1500 Sq. ft. |  | 4 | 6.8 | 8.9 | 11 | 13 | 15.1 | 17.64 | 20.16
| 1501 to 3000 Sq. ft. |  | 5.5 | 9.4 | 13.2 | 16.5 | 18.7 | 22.1 | 25.025 | 28.6
| Greater than 3000 Sq. ft. |  | 7.5 | 12.8 | 18 | 22.5 | 25.5 | 30.1 | 34.1 | 39
COOLING LOAD IN kVA
| AC Load (tons) |  | Number of Homes 1: Number of Homes
|  | Space Cooled | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |  |  |  |  | 1800 | 2100
| 1 | 500 | Number of Homes 1: 2
| 1.5 | 900 | Number of Homes 1: 3
| 2 | 1200 | Number of Homes 1: 4
| 2.5 | 1500 | 5 | 9 | 12.8 | 16.4 | 19.5 | 23.1 | 27 | 30
| 3 | 1800 | 5.5 | 9.9 | 14 | 18 | 21.5 | 25.4 | 29.6 | 33
| 3.5 | 2100 | 7 | 12.6 | 17.9 | 23 | 27.3 | 32.3 | 37.7 | 42
| 4 | 2400 | 8 | 14.4 | 20.4 | 26.2 | 31.2 | 37 | 43.1 | 48
| 5 | 3000 | 10 | 18 | 25.5 | 32.8 | 39 | 46.2 | 53.9 | 60
HEATING LOAD IN kVA
| Heat Pump (tons) |  | Number of Homes 1: Number of Homes
|  | Space Heated | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
| 1 | 500 | Number of Homes 1: 5
| 1.5 | 900 | Number of Homes 1: 5
| 2 | 1200 | Number of Homes 1: 6
| 2.5 | 1500 | 8 | 14.4 | 20.4 | 26.2 | 31.2 | 37 | 43.1 | 48
| 3 | 1800 | 9 | 16.2 | 23 | 29.5 | 35.1 | 41.6 | 48.5 | 54
| 3.5 | 2100 | 10.5 | 18.9 | 26.8 | 34.4 | 41 | 48.5 | 56.6 | 63
| 4 | 2400 | 12.5 | 22.5 | 31.9 | 41 | 48.8 | 57.8 | 67.4 | 75
| 5 | 3000 | 16 | 28.8 | 40.8 | 52.5 | 62.4 | 73.9 | 86.2 | 96
|  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
|  |  | 12.5 | 22 | 31.1 | 39.5 | 46 | 54.4 | 62.725 | 70.6
|  |  | 12.5 | 25 | 37.5 | 50 | 62.5 | 75 | 87.5 | 100
|  |  | 1 | 0.88 | 0.82933 | 0.79 | 0.736 | 0.72533 | 0.71686 | 0.706 | 0.7 | 0.7
|  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
|  |  | 16 | 28.3 | 40 | 50.9 | 59.7 | 70.6 | 81.625 | 91.6
|  |  | 16 | 32 | 48 | 64 | 80 | 96 | 112 | 128
|  |  | 1 | 0.88437 | 0.83333 | 0.79531 | 0.74625 | 0.73542 | 0.72879 | 0.71562 | 0.7 | 0.7
TRANSFORMER SIZING WORKSHEET

## Voltage Flicker Data (hidden)
VOLTAGE FLICKER DATA
|  |  | % Voltage Flicker through Distribution Transformer (kVA) (RECALCULATED) | [8 empty] | % Voltage Flicker Through 100 Feet of Secondary Cable
| A/C tons | LRA | 10 | 15 | 25 | 37.5 | 50 | 75 | 100 | 167 | User Def | 4 TPX | 2 TPX | 1/0 TPX | 4/0 TPX | 2/0 URD | 4/0 URD | 350 URD | 500 URD
| 1 | 35 | 1.7609 | 1.0638 | 0.60919 | 0.4023 | 0.28316 | 0.17801 | 0.15014 | 0.097828 | #DIV/0! | 1.3 | 0.83 | 0.54 | 0.29 | 0.44 | 0.29 | 0.19 | 0.15
| 1.5 | 48 | 2.415 | 1.4589 | 0.83546 | 0.55172 | 0.38833 | 0.24413 | 0.20591 | 0.13416 | #DIV/0! | 1.78 | 1.14 | 0.74 | 0.39 | 0.6 | 0.4 | 0.26 | 0.2
| 2 | 61 | 3.069 | 1.854 | 1.0617 | 0.70115 | 0.4935 | 0.31025 | 0.26168 | 0.1705 | #DIV/0! | 2.27 | 1.45 | 0.94 | 0.5 | 0.77 | 0.51 | 0.34 | 0.26
| 2.5 | 75 | 3.7734 | 2.2795 | 1.3054 | 0.86207 | 0.60677 | 0.38145 | 0.32174 | 0.20963 | #DIV/0! | 2.78 | 1.78 | 1.16 | 0.61 | 0.94 | 0.62 | 0.41 | 0.31
| 3 | 86 | 4.3268 | 2.6139 | 1.4969 | 0.98851 | 0.69576 | 0.4374 | 0.36893 | 0.24038 | #DIV/0! | 3.19 | 2.04 | 1.33 | 0.7 | 1.08 | 0.71 | 0.47 | 0.36
| 3.5 | 97 | 4.8802 | 2.9482 | 1.6883 | 1.1149 | 0.78475 | 0.49335 | 0.41612 | 0.27112 | #DIV/0! | 3.6 | 2.3 | 1.49 | 0.79 | 1.22 | 0.81 | 0.53 | 0.41
| 4 | 118 | 5.9368 | 3.5865 | 2.0538 | 1.3563 | 0.95464 | 0.60016 | 0.5062 | 0.32982 | #DIV/0! | 4.38 | 2.8 | 1.82 | 0.96 | 1.48 | 0.98 | 0.65 | 0.49
| 5 | 140 | 7.0436 | 4.2551 | 2.4368 | 1.6092 | 1.1326 | 0.71205 | 0.60058 | 0.39131 | #DIV/0! | 5.2 | 3.33 | 2.16 | 1.14 | 1.76 | 1.16 | 0.77 | 0.59
% Voltage Flicker through Distribution Transformer (kVA) (OLD)
| A/C tons | LRA | 10 | 15 | 25 | 37.5 | 50 | 75 | 100 | 167
| 1 | 35 | 1.75 | 1.06 | 0.6 | 0.39 | 0.26 | 0.16 | 0.13 | 0.08
| 1.5 | 48 | 2.4 | 1.46 | 0.82 | 0.53 | 0.36 | 0.22 | 0.18 | 0.11
| 2 | 61 | 3.06 | 1.85 | 1.04 | 0.68 | 0.45 | 0.29 | 0.23 | 0.15
| 2.5 | 75 | 3.76 | 2.28 | 1.28 | 0.83 | 0.56 | 0.35 | 0.28 | 0.18
| 3 | 86 | 4.31 | 2.61 | 1.47 | 0.96 | 0.64 | 0.4 | 0.32 | 0.2
| 3.5 | 97 | 4.86 | 2.94 | 1.66 | 1.08 | 0.72 | 0.45 | 0.36 | 0.23
| 4 | 118 | 5.91 | 3.58 | 2.02 | 1.31 | 0.87 | 0.55 | 0.44 | 0.28
| 5 | 140 | 7.01 | 4.25 | 2.4 | 1.56 | 1.04 | 0.65 | 0.52 | 0.33
USER INPUT

## Voltage Drop Table (hidden)
VOLTAGE DROP TABLE
|  | % Voltage Drop through Padmounted Transf. | [8 empty] | % Voltage Drop Through 100 Feet of
Load |  | Transformer kVA | [8 empty] | Secondary Conductors
(kVA) | Amps | 10 | 15 | 25 | 37.5 | 50 | 75 | 100 | 167 | User Defined Impedance | 4 TPX | 2 TPX | 1/0 TPX | 4/0 TPX | 2/0 URD | 4/0 URD | 350 URD | 500 URD
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 4 | 0.20123 | 0.12143 | 0.066842 | 0.04303 | 0.028124 | 0.017765 | 0.014038 | 0.0088589 | 0 | 0.15607 | 0.099468 | 0.064112 | 0.03355 | 0.051957 | 0.034038 | 0.022146 | 0.016629
2 | 8 | 0.40246 | 0.24285 | 0.13368 | 0.086059 | 0.056247 | 0.03553 | 0.028077 | 0.017718 | 0 | 0.31214 | 0.19894 | 0.12822 | 0.067101 | 0.10391 | 0.068077 | 0.044291 | 0.033259
3 | 13 | 0.654 | 0.39464 | 0.21723 | 0.13985 | 0.091402 | 0.057736 | 0.045625 | 0.028791 | 0 | 0.50723 | 0.32327 | 0.20836 | 0.10904 | 0.16886 | 0.11062 | 0.071973 | 0.054046
4 | 17 | 0.85523 | 0.51606 | 0.28408 | 0.18288 | 0.11953 | 0.075501 | 0.059663 | 0.03765 | 0 | 0.6633 | 0.42274 | 0.27248 | 0.14259 | 0.22082 | 0.14466 | 0.094119 | 0.070675
5 | 21 | 1.0565 | 0.63749 | 0.35092 | 0.22591 | 0.14765 | 0.093265 | 0.073701 | 0.046509 | 0 | 0.81938 | 0.52221 | 0.33659 | 0.17614 | 0.27278 | 0.1787 | 0.11626 | 0.087304
6 | 25 | 1.2577 | 0.75892 | 0.41776 | 0.26894 | 0.17577 | 0.11103 | 0.08774 | 0.055368 | 0 | 0.97545 | 0.62168 | 0.4007 | 0.20969 | 0.32473 | 0.21274 | 0.13841 | 0.10393
7 | 29 | 1.4589 | 0.88035 | 0.4846 | 0.31197 | 0.2039 | 0.1288 | 0.10178 | 0.064227 | 0 | 1.1315 | 0.72115 | 0.46481 | 0.24324 | 0.37669 | 0.24678 | 0.16056 | 0.12056
8 | 33 | 1.6601 | 1.0018 | 0.55144 | 0.35499 | 0.23202 | 0.14656 | 0.11582 | 0.073086 | 0 | 1.2876 | 0.82061 | 0.52892 | 0.27679 | 0.42865 | 0.28082 | 0.1827 | 0.13719
9 | 38 | 1.9117 | 1.1536 | 0.63499 | 0.40878 | 0.26718 | 0.16877 | 0.13336 | 0.08416 | 0 | 1.4827 | 0.94495 | 0.60906 | 0.31873 | 0.49359 | 0.32336 | 0.21038 | 0.15798
10 | 42 | 2.1129 | 1.275 | 0.70184 | 0.45181 | 0.2953 | 0.18653 | 0.1474 | 0.093018 | 0 | 1.6388 | 1.0444 | 0.67317 | 0.35228 | 0.54555 | 0.3574 | 0.23253 | 0.17461
11 | 46 | 2.3141 | 1.3964 | 0.76868 | 0.49484 | 0.32342 | 0.2043 | 0.16144 | 0.10188 | 0 | 1.7948 | 1.1439 | 0.73729 | 0.38583 | 0.59751 | 0.39144 | 0.25468 | 0.19124
12 | 50 | 2.5154 | 1.5178 | 0.83552 | 0.53787 | 0.35155 | 0.22206 | 0.17548 | 0.11074 | 0 | 1.9509 | 1.2434 | 0.8014 | 0.41938 | 0.64946 | 0.42548 | 0.27682 | 0.20787
13 | 54 | 2.7166 | 1.6393 | 0.90236 | 0.5809 | 0.37967 | 0.23983 | 0.18952 | 0.1196 | 0 | 2.107 | 1.3428 | 0.86551 | 0.45293 | 0.70142 | 0.45952 | 0.29897 | 0.2245
14 | 58 | 2.9178 | 1.7607 | 0.9692 | 0.62393 | 0.40779 | 0.25759 | 0.20356 | 0.12845 | 0 | 2.263 | 1.4423 | 0.92962 | 0.48648 | 0.75338 | 0.49356 | 0.32111 | 0.24113
15 | 63 | 3.1694 | 1.9125 | 1.0528 | 0.67772 | 0.44295 | 0.2798 | 0.2211 | 0.13953 | 0 | 2.4581 | 1.5666 | 1.0098 | 0.52842 | 0.81833 | 0.5361 | 0.34879 | 0.26191
16 | 67 | 3.3706 | 2.0339 | 1.1196 | 0.72075 | 0.47107 | 0.29756 | 0.23514 | 0.14839 | 0 | 2.6142 | 1.6661 | 1.0739 | 0.56197 | 0.87028 | 0.57014 | 0.37094 | 0.27854
17 | 71 | 3.5718 | 2.1553 | 1.1864 | 0.76378 | 0.4992 | 0.31533 | 0.24918 | 0.15725 | 0 | 2.7703 | 1.7656 | 1.138 | 0.59552 | 0.92224 | 0.60418 | 0.39309 | 0.29517
18 | 75 | 3.7731 | 2.2768 | 1.2533 | 0.80681 | 0.52732 | 0.33309 | 0.26322 | 0.1661 | 0 | 2.9263 | 1.865 | 1.2021 | 0.62907 | 0.9742 | 0.63822 | 0.41523 | 0.3118
19 | 79 | 3.9743 | 2.3982 | 1.3201 | 0.84984 | 0.55544 | 0.35086 | 0.27726 | 0.17496 | 0 | 3.0824 | 1.9645 | 1.2662 | 0.66262 | 1.0262 | 0.67226 | 0.43738 | 0.32843
20 | 83 | 4.1755 | 2.5196 | 1.387 | 0.89287 | 0.58357 | 0.36862 | 0.2913 | 0.18382 | 0 | 3.2385 | 2.064 | 1.3303 | 0.69617 | 1.0781 | 0.70629 | 0.45952 | 0.34506
21 | 88 | 4.4271 | 2.6714 | 1.4705 | 0.94665 | 0.61872 | 0.39083 | 0.30884 | 0.1949 | 0 | 3.4336 | 2.1883 | 1.4105 | 0.73811 | 1.1431 | 0.74884 | 0.4872 | 0.36585
22 | 92 | 4.6283 | 2.7928 | 1.5374 | 0.98968 | 0.64685 | 0.40859 | 0.32288 | 0.20375 | 0 | 3.5896 | 2.2878 | 1.4746 | 0.77166 | 1.195 | 0.78288 | 0.50935 | 0.38248
23 | 96 | 4.8295 | 2.9142 | 1.6042 | 1.0327 | 0.67497 | 0.42636 | 0.33692 | 0.21261 | 0 | 3.7457 | 2.3872 | 1.5387 | 0.80521 | 1.247 | 0.81692 | 0.5315 | 0.39911
24 | 100 | 5.0308 | 3.0357 | 1.671 | 1.0757 | 0.70309 | 0.44412 | 0.35096 | 0.22147 | 0 | 3.9018 | 2.4867 | 1.6028 | 0.83876 | 1.2989 | 0.85096 | 0.55364 | 0.41574
25 | 104 | 5.232 | 3.1571 | 1.7379 | 1.1188 | 0.73122 | 0.46189 | 0.365 | 0.23033 | 0 | 4.0579 | 2.5862 | 1.6669 | 0.87231 | 1.3509 | 0.885 | 0.57579 | 0.43236
26 | 108 | 5.4332 | 3.2785 | 1.8047 | 1.1618 | 0.75934 | 0.47965 | 0.37904 | 0.23919 | 0 | 4.2139 | 2.6856 | 1.731 | 0.90586 | 1.4028 | 0.91903 | 0.59793 | 0.44899
27 | 113 | 5.6848 | 3.4303 | 1.8883 | 1.2156 | 0.7945 | 0.50186 | 0.39658 | 0.25026 | 0 | 4.409 | 2.81 | 1.8112 | 0.9478 | 1.4678 | 0.96158 | 0.62561 | 0.46978
28 | 117 | 5.886 | 3.5517 | 1.9551 | 1.2586 | 0.82262 | 0.51962 | 0.41062 | 0.25912 | 0 | 4.5651 | 2.9094 | 1.8753 | 0.98135 | 1.5197 | 0.99562 | 0.64776 | 0.48641
29 | 121 | 6.0872 | 3.6732 | 2.022 | 1.3016 | 0.85074 | 0.53739 | 0.42466 | 0.26798 | 0 | 4.7212 | 3.0089 | 1.9394 | 1.0149 | 1.5717 | 1.0297 | 0.66991 | 0.50304
30 | 125 | 6.2884 | 3.7946 | 2.0888 | 1.3447 | 0.87887 | 0.55515 | 0.4387 | 0.27684 | 0 | 4.8772 | 3.1084 | 2.0035 | 1.0484 | 1.6237 | 1.0637 | 0.69205 | 0.51967
31 | 129 | 6.4897 | 3.916 | 2.1556 | 1.3877 | 0.90699 | 0.57292 | 0.45274 | 0.2857 | 0 | 5.0333 | 3.2079 | 2.0676 | 1.082 | 1.6756 | 1.0977 | 0.7142 | 0.5363
32 | 133 | 6.6909 | 4.0374 | 2.2225 | 1.4307 | 0.93511 | 0.59068 | 0.46678 | 0.29456 | 0 | 5.1894 | 3.3073 | 2.1317 | 1.1155 | 1.7276 | 1.1318 | 0.73634 | 0.55293
33 | 138 | 6.9424 | 4.1892 | 2.306 | 1.4845 | 0.97027 | 0.61289 | 0.48432 | 0.30563 | 0 | 5.3845 | 3.4317 | 2.2119 | 1.1575 | 1.7925 | 1.1743 | 0.76403 | 0.57371
34 | 142 | 7.1437 | 4.3107 | 2.3729 | 1.5276 | 0.99839 | 0.63065 | 0.49836 | 0.31449 | 0 | 5.5405 | 3.5311 | 2.276 | 1.191 | 1.8445 | 1.2084 | 0.78617 | 0.59034
35 | 146 | 7.3449 | 4.4321 | 2.4397 | 1.5706 | 1.0265 | 0.64842 | 0.5124 | 0.32335 | 0 | 5.6966 | 3.6306 | 2.3401 | 1.2246 | 1.8964 | 1.2424 | 0.80832 | 0.60697
36 | 150 | 7.5461 | 4.5535 | 2.5066 | 1.6136 | 1.0546 | 0.66618 | 0.52644 | 0.33221 | 0 | 5.8527 | 3.7301 | 2.4042 | 1.2581 | 1.9484 | 1.2764 | 0.83046 | 0.6236
37 | 154 | 7.7474 | 4.6749 | 2.5734 | 1.6566 | 1.0828 | 0.68395 | 0.54048 | 0.34107 | 0 | 6.0088 | 3.8295 | 2.4683 | 1.2917 | 2.0004 | 1.3105 | 0.85261 | 0.64023
38 | 158 | 7.9486 | 4.7964 | 2.6402 | 1.6997 | 1.1109 | 0.70171 | 0.55451 | 0.34993 | 0 | 6.1648 | 3.929 | 2.5324 | 1.3252 | 2.0523 | 1.3445 | 0.87475 | 0.65686
39 | 163 | 8.2001 | 4.9481 | 2.7238 | 1.7535 | 1.146 | 0.72392 | 0.57206 | 0.361 | 0 | 6.3599 | 4.0533 | 2.6126 | 1.3672 | 2.1173 | 1.3871 | 0.90244 | 0.67765
40 | 167 | 8.4014 | 5.0696 | 2.7906 | 1.7965 | 1.1742 | 0.74168 | 0.5861 | 0.36986 | 0 | 6.516 | 4.1528 | 2.6767 | 1.4007 | 2.1692 | 1.4211 | 0.92458 | 0.69428
41 | 171 | 8.6026 | 5.191 | 2.8575 | 1.8395 | 1.2023 | 0.75945 | 0.60014 | 0.37872 | 0 | 6.6721 | 4.2523 | 2.7408 | 1.4343 | 2.2212 | 1.4551 | 0.94673 | 0.71091
42 | 175 | 8.8038 | 5.3124 | 2.9243 | 1.8825 | 1.2304 | 0.77721 | 0.61418 | 0.38758 | 0 | 6.8281 | 4.3517 | 2.8049 | 1.4678 | 2.2731 | 1.4892 | 0.96887 | 0.72754
43 | 179 | 9.005 | 5.4339 | 2.9912 | 1.9256 | 1.2585 | 0.79498 | 0.62822 | 0.39644 | 0 | 6.9842 | 4.4512 | 2.869 | 1.5014 | 2.3251 | 1.5232 | 0.99102 | 0.74417
44 | 183 | 9.2063 | 5.5553 | 3.058 | 1.9686 | 1.2867 | 0.81274 | 0.64225 | 0.40529 | 0 | 7.1403 | 4.5507 | 2.9331 | 1.5349 | 2.377 | 1.5573 | 1.0132 | 0.7608
45 | 188 | 9.4578 | 5.7071 | 3.1416 | 2.0224 | 1.3218 | 0.83495 | 0.6598 | 0.41637 | 0 | 7.3354 | 4.675 | 3.0133 | 1.5769 | 2.442 | 1.5998 | 1.0408 | 0.78158
46 | 192 | 9.659 | 5.8285 | 3.2084 | 2.0654 | 1.3499 | 0.85271 | 0.67384 | 0.42523 | 0 | 7.4914 | 4.7745 | 3.0774 | 1.6104 | 2.4939 | 1.6338 | 1.063 | 0.79821
47 | 196 | 9.8603 | 5.9499 | 3.2752 | 2.1085 | 1.3781 | 0.87048 | 0.68788 | 0.43409 | 0 | 7.6475 | 4.8739 | 3.1415 | 1.644 | 2.5459 | 1.6679 | 1.0851 | 0.81484
48 | 200 | 10.0615 | 6.0713 | 3.3421 | 2.1515 | 1.4062 | 0.88824 | 0.70192 | 0.44294 | 0 | 7.8036 | 4.9734 | 3.2056 | 1.6775 | 2.5979 | 1.7019 | 1.1073 | 0.83147
49 | 204 | 10.2627 | 6.1928 | 3.4089 | 2.1945 | 1.4343 | 0.90601 | 0.71596 | 0.4518 | 0 | 7.9597 | 5.0729 | 3.2697 | 1.7111 | 2.6498 | 1.736 | 1.1294 | 0.8481
50 | 208 | 10.464 | 6.3142 | 3.4758 | 2.2375 | 1.4624 | 0.92377 | 0.72999 | 0.46066 | 0 | 8.1157 | 5.1724 | 3.3338 | 1.7446 | 2.7018 | 1.77 | 1.1516 | 0.86473
51 | 213 | 10.7155 | 6.466 | 3.5593 | 2.2913 | 1.4976 | 0.94598 | 0.74754 | 0.47174 | 0 | 8.3108 | 5.2967 | 3.414 | 1.7866 | 2.7667 | 1.8125 | 1.1793 | 0.88552
52 | 217 | 10.9167 | 6.5874 | 3.6262 | 2.3344 | 1.5257 | 0.96374 | 0.76158 | 0.4806 | 0 | 8.4669 | 5.3962 | 3.4781 | 1.8201 | 2.8187 | 1.8466 | 1.2014 | 0.90215
53 | 221 | 11.118 | 6.7088 | 3.693 | 2.3774 | 1.5538 | 0.98151 | 0.77562 | 0.48945 | 0 | 8.623 | 5.4956 | 3.5422 | 1.8537 | 2.8706 | 1.8806 | 1.2235 | 0.91878
54 | 225 | 11.3192 | 6.8303 | 3.7598 | 2.4204 | 1.582 | 0.99927 | 0.78966 | 0.49831 | 0 | 8.779 | 5.5951 | 3.6063 | 1.8872 | 2.9226 | 1.9147 | 1.2457 | 0.9354
55 | 229 | 11.5204 | 6.9517 | 3.8267 | 2.4634 | 1.6101 | 1.017 | 0.8037 | 0.50717 | 0 | 8.9351 | 5.6946 | 3.6704 | 1.9208 | 2.9745 | 1.9487 | 1.2678 | 0.95203
56 | 233 | 11.7217 | 7.0731 | 3.8935 | 2.5065 | 1.6382 | 1.0348 | 0.81773 | 0.51603 | 0 | 9.0912 | 5.794 | 3.7345 | 1.9543 | 3.0265 | 1.9827 | 1.29 | 0.96866
57 | 238 | 11.9732 | 7.2249 | 3.9771 | 2.5603 | 1.6734 | 1.057 | 0.83528 | 0.5271 | 0 | 9.2863 | 5.9184 | 3.8147 | 1.9962 | 3.0915 | 2.0253 | 1.3177 | 0.98945
58 | 242 | 12.1744 | 7.3463 | 4.0439 | 2.6033 | 1.7015 | 1.0748 | 0.84932 | 0.53596 | 0 | 9.4423 | 6.0178 | 3.8788 | 2.0298 | 3.1434 | 2.0593 | 1.3398 | 1.0061
59 | 246 | 12.3757 | 7.4678 | 4.1108 | 2.6463 | 1.7296 | 1.0925 | 0.86336 | 0.54482 | 0 | 9.5984 | 6.1173 | 3.9429 | 2.0633 | 3.1954 | 2.0934 | 1.362 | 1.0227
60 | 250 | 12.5769 | 7.5892 | 4.1776 | 2.6894 | 1.7577 | 1.1103 | 0.8774 | 0.55368 | 0 | 9.7545 | 6.2168 | 4.007 | 2.0969 | 3.2473 | 2.1274 | 1.3841 | 1.0393
61 | 254 | 12.7781 | 7.7106 | 4.2444 | 2.7324 | 1.7859 | 1.1281 | 0.89144 | 0.56254 | 0 | 9.9106 | 6.3162 | 4.0711 | 2.1304 | 3.2993 | 2.1614 | 1.4062 | 1.056
62 | 258 | 12.9793 | 7.832 | 4.3113 | 2.7754 | 1.814 | 1.1458 | 0.90547 | 0.5714 | 0 | 10.0666 | 6.4157 | 4.1352 | 2.164 | 3.3512 | 2.1955 | 1.4284 | 1.0726
63 | 263 | 13.2309 | 7.9838 | 4.3948 | 2.8292 | 1.8491 | 1.168 | 0.92302 | 0.58247 | 0 | 10.2617 | 6.54 | 4.2154 | 2.2059 | 3.4162 | 2.238 | 1.4561 | 1.0934
64 | 267 | 13.4321 | 8.1052 | 4.4617 | 2.8722 | 1.8773 | 1.1858 | 0.93706 | 0.59133 | 0 | 10.4178 | 6.6395 | 4.2795 | 2.2395 | 3.4681 | 2.2721 | 1.4782 | 1.11
65 | 271 | 13.6333 | 8.2267 | 4.5285 | 2.9153 | 1.9054 | 1.2036 | 0.9511 | 0.60019 | 0 | 10.5739 | 6.739 | 4.3436 | 2.273 | 3.5201 | 2.3061 | 1.5004 | 1.1266
66 | 275 | 13.8346 | 8.3481 | 4.5954 | 2.9583 | 1.9335 | 1.2213 | 0.96514 | 0.60905 | 0 | 10.7299 | 6.8384 | 4.4077 | 2.3066 | 3.5721 | 2.3401 | 1.5225 | 1.1433
67 | 279 | 14.0358 | 8.4695 | 4.6622 | 3.0013 | 1.9616 | 1.2391 | 0.97917 | 0.61791 | 0 | 10.886 | 6.9379 | 4.4718 | 2.3401 | 3.624 | 2.3742 | 1.5447 | 1.1599
68 | 283 | 14.237 | 8.591 | 4.729 | 3.0443 | 1.9898 | 1.2569 | 0.99321 | 0.62677 | 0 | 11.0421 | 7.0374 | 4.5359 | 2.3737 | 3.676 | 2.4082 | 1.5668 | 1.1765
69 | 288 | 14.4886 | 8.7427 | 4.8126 | 3.0981 | 2.0249 | 1.2791 | 1.0108 | 0.63784 | 0 | 11.2372 | 7.1617 | 4.6161 | 2.4156 | 3.7409 | 2.4508 | 1.5945 | 1.1973
70 | 292 | 14.6898 | 8.8642 | 4.8794 | 3.1412 | 2.053 | 1.2968 | 1.0248 | 0.6467 | 0 | 11.3932 | 7.2612 | 4.6802 | 2.4492 | 3.7929 | 2.4848 | 1.6166 | 1.2139
71 | 296 | 14.891 | 8.9856 | 4.9463 | 3.1842 | 2.0812 | 1.3146 | 1.0388 | 0.65556 | 0 | 11.5493 | 7.3607 | 4.7443 | 2.4827 | 3.8448 | 2.5188 | 1.6388 | 1.2306
72 | 300 | 15.0923 | 9.107 | 5.0131 | 3.2272 | 2.1093 | 1.3324 | 1.0529 | 0.66442 | 0 | 11.7054 | 7.4601 | 4.8084 | 2.5163 | 3.8968 | 2.5529 | 1.6609 | 1.2472
73 | 304 | 15.2935 | 9.2284 | 5.08 | 3.2703 | 2.1374 | 1.3501 | 1.0669 | 0.67328 | 0 | 11.8615 | 7.5596 | 4.8725 | 2.5498 | 3.9487 | 2.5869 | 1.6831 | 1.2638
74 | 308 | 15.4947 | 9.3499 | 5.1468 | 3.3133 | 2.1655 | 1.3679 | 1.081 | 0.68214 | 0 | 12.0175 | 7.6591 | 4.9366 | 2.5834 | 4.0007 | 2.6209 | 1.7052 | 1.2805
75 | 313 | 15.7463 | 9.5017 | 5.2303 | 3.3671 | 2.2007 | 1.3901 | 1.0985 | 0.69321 | 0 | 12.2126 | 7.7834 | 5.0168 | 2.6253 | 4.0657 | 2.6635 | 1.7329 | 1.3013
76 | 317 | 15.9475 | 9.6231 | 5.2972 | 3.4101 | 2.2288 | 1.4079 | 1.1125 | 0.70207 | 0 | 12.3687 | 7.8829 | 5.0809 | 2.6589 | 4.1176 | 2.6975 | 1.755 | 1.3179
77 | 321 | 16.1487 | 9.7445 | 5.364 | 3.4531 | 2.2569 | 1.4256 | 1.1266 | 0.71093 | 0 | 12.5248 | 7.9823 | 5.145 | 2.6924 | 4.1696 | 2.7316 | 1.7772 | 1.3345
78 | 325 | 16.3499 | 9.8659 | 5.4309 | 3.4962 | 2.2851 | 1.4434 | 1.1406 | 0.71979 | 0 | 12.6808 | 8.0818 | 5.2091 | 2.726 | 4.2215 | 2.7656 | 1.7993 | 1.3511
79 | 329 | 16.5512 | 9.9874 | 5.4977 | 3.5392 | 2.3132 | 1.4612 | 1.1547 | 0.72864 | 0 | 12.8369 | 8.1813 | 5.2732 | 2.7595 | 4.2735 | 2.7997 | 1.8215 | 1.3678
80 | 333 | 16.7524 | 10.1088 | 5.5646 | 3.5822 | 2.3413 | 1.4789 | 1.1687 | 0.7375 | 0 | 12.993 | 8.2807 | 5.3373 | 2.7931 | 4.3254 | 2.8337 | 1.8436 | 1.3844
81 | 338 | 17.0039 | 10.2606 | 5.6481 | 3.636 | 2.3765 | 1.5011 | 1.1862 | 0.74858 | 0 | 13.1881 | 8.4051 | 5.4175 | 2.835 | 4.3904 | 2.8762 | 1.8713 | 1.4052
82 | 342 | 17.2052 | 10.382 | 5.715 | 3.679 | 2.4046 | 1.5189 | 1.2003 | 0.75744 | 0 | 13.3441 | 8.5045 | 5.4816 | 2.8686 | 4.4423 | 2.9103 | 1.8935 | 1.4218
83 | 346 | 17.4064 | 10.5034 | 5.7818 | 3.7221 | 2.4327 | 1.5367 | 1.2143 | 0.76629 | 0 | 13.5002 | 8.604 | 5.5457 | 2.9021 | 4.4943 | 2.9443 | 1.9156 | 1.4384
84 | 350 | 17.6076 | 10.6249 | 5.8486 | 3.7651 | 2.4608 | 1.5544 | 1.2284 | 0.77515 | 0 | 13.6563 | 8.7035 | 5.6098 | 2.9357 | 4.5463 | 2.9784 | 1.9377 | 1.4551
85 | 354 | 17.8089 | 10.7463 | 5.9155 | 3.8081 | 2.489 | 1.5722 | 1.2424 | 0.78401 | 0 | 13.8123 | 8.8029 | 5.6739 | 2.9692 | 4.5982 | 3.0124 | 1.9599 | 1.4717
86 | 358 | 18.0101 | 10.8677 | 5.9823 | 3.8512 | 2.5171 | 1.59 | 1.2564 | 0.79287 | 0 | 13.9684 | 8.9024 | 5.738 | 3.0028 | 4.6502 | 3.0464 | 1.982 | 1.4883
87 | 363 | 18.2616 | 11.0195 | 6.0659 | 3.9049 | 2.5522 | 1.6122 | 1.274 | 0.80395 | 0 | 14.1635 | 9.0267 | 5.8182 | 3.0447 | 4.7151 | 3.089 | 2.0097 | 1.5091
88 | 367 | 18.4629 | 11.1409 | 6.1327 | 3.948 | 2.5804 | 1.6299 | 1.288 | 0.8128 | 0 | 14.3196 | 9.1262 | 5.8823 | 3.0782 | 4.7671 | 3.123 | 2.0319 | 1.5257
89 | 371 | 18.6641 | 11.2623 | 6.1996 | 3.991 | 2.6085 | 1.6477 | 1.3021 | 0.82166 | 0 | 14.4757 | 9.2257 | 5.9464 | 3.1118 | 4.819 | 3.1571 | 2.054 | 1.5424
90 | 375 | 18.8653 | 11.3838 | 6.2664 | 4.034 | 2.6366 | 1.6655 | 1.3161 | 0.83052 | 0 | 14.6317 | 9.3252 | 6.0105 | 3.1453 | 4.871 | 3.1911 | 2.0762 | 1.559
91 | 379 | 19.0666 | 11.5052 | 6.3332 | 4.0771 | 2.6647 | 1.6832 | 1.3301 | 0.83938 | 0 | 14.7878 | 9.4246 | 6.0746 | 3.1789 | 4.9229 | 3.2251 | 2.0983 | 1.5756
92 | 383 | 19.2678 | 11.6266 | 6.4001 | 4.1201 | 2.6928 | 1.701 | 1.3442 | 0.84824 | 0 | 14.9439 | 9.5241 | 6.1387 | 3.2124 | 4.9749 | 3.2592 | 2.1204 | 1.5923
93 | 388 | 19.5193 | 11.7784 | 6.4836 | 4.1739 | 2.728 | 1.7232 | 1.3617 | 0.85931 | 0 | 15.139 | 9.6484 | 6.2189 | 3.2544 | 5.0398 | 3.3017 | 2.1481 | 1.6131
94 | 392 | 19.7205 | 11.8998 | 6.5505 | 4.2169 | 2.7561 | 1.741 | 1.3758 | 0.86817 | 0 | 15.295 | 9.7479 | 6.283 | 3.2879 | 5.0918 | 3.3358 | 2.1703 | 1.6297
95 | 396 | 19.9218 | 12.0213 | 6.6173 | 4.2599 | 2.7842 | 1.7587 | 1.3898 | 0.87703 | 0 | 15.4511 | 9.8474 | 6.3471 | 3.3215 | 5.1438 | 3.3698 | 2.1924 | 1.6463
96 | 400 | 20.123 | 12.1427 | 6.6842 | 4.303 | 2.8124 | 1.7765 | 1.4038 | 0.88589 | 0 | 15.6072 | 9.9468 | 6.4112 | 3.355 | 5.1957 | 3.4038 | 2.2146 | 1.6629
97 | 404 | 20.3242 | 12.2641 | 6.751 | 4.346 | 2.8405 | 1.7942 | 1.4179 | 0.89475 | 0 | 15.7632 | 10.0463 | 6.4753 | 3.3886 | 5.2477 | 3.4379 | 2.2367 | 1.6796
98 | 408 | 20.5255 | 12.3855 | 6.8178 | 4.389 | 2.8686 | 1.812 | 1.4319 | 0.90361 | 0 | 15.9193 | 10.1458 | 6.5394 | 3.4221 | 5.2996 | 3.4719 | 2.2589 | 1.6962
99 | 413 | 20.777 | 12.5373 | 6.9014 | 4.4428 | 2.9038 | 1.8342 | 1.4495 | 0.91468 | 0 | 16.1144 | 10.2701 | 6.6196 | 3.4641 | 5.3646 | 3.5145 | 2.2865 | 1.717
100 | 417 | 20.9782 | 12.6588 | 6.9682 | 4.4858 | 2.9319 | 1.852 | 1.4635 | 0.92354 | 0 | 16.2705 | 10.3696 | 6.6837 | 3.4976 | 5.4165 | 3.5485 | 2.3087 | 1.7336
101 | 421 | 21.1795 | 12.7802 | 7.0351 | 4.5289 | 2.96 | 1.8697 | 1.4775 | 0.9324 | 0 | 16.4265 | 10.469 | 6.7478 | 3.5312 | 5.4685 | 3.5825 | 2.3308 | 1.7502
102 | 425 | 21.3807 | 12.9016 | 7.1019 | 4.5719 | 2.9881 | 1.8875 | 1.4916 | 0.94126 | 0 | 16.5826 | 10.5685 | 6.8119 | 3.5647 | 5.5205 | 3.6166 | 2.353 | 1.7669
103 | 429 | 21.5819 | 13.023 | 7.1688 | 4.6149 | 3.0163 | 1.9053 | 1.5056 | 0.95012 | 0 | 16.7387 | 10.668 | 6.876 | 3.5983 | 5.5724 | 3.6506 | 2.3751 | 1.7835
104 | 433 | 21.7832 | 13.1445 | 7.2356 | 4.658 | 3.0444 | 1.923 | 1.5197 | 0.95898 | 0 | 16.8948 | 10.7674 | 6.9401 | 3.6318 | 5.6244 | 3.6846 | 2.3973 | 1.8001
105 | 438 | 22.0347 | 13.2962 | 7.3191 | 4.7117 | 3.0795 | 1.9452 | 1.5372 | 0.97005 | 0 | 17.0899 | 10.8918 | 7.0203 | 3.6738 | 5.6893 | 3.7272 | 2.4249 | 1.8209
106 | 442 | 22.2359 | 13.4177 | 7.386 | 4.7548 | 3.1077 | 1.963 | 1.5512 | 0.97891 | 0 | 17.2459 | 10.9912 | 7.0844 | 3.7073 | 5.7413 | 3.7612 | 2.4471 | 1.8376
107 | 446 | 22.4372 | 13.5391 | 7.4528 | 4.7978 | 3.1358 | 1.9808 | 1.5653 | 0.98777 | 0 | 17.402 | 11.0907 | 7.1485 | 3.7409 | 5.7932 | 3.7953 | 2.4692 | 1.8542
108 | 450 | 22.6384 | 13.6605 | 7.5197 | 4.8408 | 3.1639 | 1.9985 | 1.5793 | 0.99663 | 0 | 17.5581 | 11.1902 | 7.2126 | 3.7744 | 5.8452 | 3.8293 | 2.4914 | 1.8708
109 | 454 | 22.8396 | 13.782 | 7.5865 | 4.8839 | 3.192 | 2.0163 | 1.5934 | 1.0055 | 0 | 17.7141 | 11.2897 | 7.2767 | 3.808 | 5.8971 | 3.8633 | 2.5135 | 1.8874
110 | 458 | 23.0408 | 13.9034 | 7.6534 | 4.9269 | 3.2202 | 2.0341 | 1.6074 | 1.0143 | 0 | 17.8702 | 11.3891 | 7.3408 | 3.8415 | 5.9491 | 3.8974 | 2.5357 | 1.9041
111 | 463 | 23.2924 | 14.0552 | 7.7369 | 4.9807 | 3.2553 | 2.0563 | 1.6249 | 1.0254 | 0 | 18.0653 | 11.5135 | 7.421 | 3.8835 | 6.014 | 3.9399 | 2.5634 | 1.9249
112 | 467 | 23.4936 | 14.1766 | 7.8037 | 5.0237 | 3.2834 | 2.074 | 1.639 | 1.0343 | 0 | 18.2214 | 11.6129 | 7.4851 | 3.917 | 6.066 | 3.974 | 2.5855 | 1.9415
113 | 471 | 23.6948 | 14.298 | 7.8706 | 5.0667 | 3.3116 | 2.0918 | 1.653 | 1.0431 | 0 | 18.3774 | 11.7124 | 7.5492 | 3.9506 | 6.118 | 4.008 | 2.6077 | 1.9581
114 | 475 | 23.8961 | 14.4194 | 7.9374 | 5.1098 | 3.3397 | 2.1096 | 1.6671 | 1.052 | 0 | 18.5335 | 11.8119 | 7.6133 | 3.9841 | 6.1699 | 4.042 | 2.6298 | 1.9747
115 | 479 | 24.0973 | 14.5409 | 8.0043 | 5.1528 | 3.3678 | 2.1273 | 1.6811 | 1.0609 | 0 | 18.6896 | 11.9113 | 7.6774 | 4.0177 | 6.2219 | 4.0761 | 2.6519 | 1.9914
116 | 483 | 24.2985 | 14.6623 | 8.0711 | 5.1958 | 3.3959 | 2.1451 | 1.6951 | 1.0697 | 0 | 18.8457 | 12.0108 | 7.7415 | 4.0512 | 6.2738 | 4.1101 | 2.6741 | 2.008
117 | 488 | 24.5501 | 14.8141 | 8.1547 | 5.2496 | 3.4311 | 2.1673 | 1.7127 | 1.0808 | 0 | 19.0407 | 12.1351 | 7.8217 | 4.0931 | 6.3388 | 4.1527 | 2.7018 | 2.0288
118 | 492 | 24.7513 | 14.9355 | 8.2215 | 5.2926 | 3.4592 | 2.1851 | 1.7267 | 1.0896 | 0 | 19.1968 | 12.2346 | 7.8858 | 4.1267 | 6.3907 | 4.1867 | 2.7239 | 2.0454
119 | 496 | 24.9525 | 15.0569 | 8.2883 | 5.3357 | 3.4873 | 2.2028 | 1.7408 | 1.0985 | 0 | 19.3529 | 12.3341 | 7.9499 | 4.1602 | 6.4427 | 4.2207 | 2.7461 | 2.062
120 | 500 | 25.1538 | 15.1784 | 8.3552 | 5.3787 | 3.5155 | 2.2206 | 1.7548 | 1.1074 | 0 | 19.509 | 12.4335 | 8.014 | 4.1938 | 6.4946 | 4.2548 | 2.7682 | 2.0787
121 | 504 | 25.355 | 15.2998 | 8.422 | 5.4217 | 3.5436 | 2.2384 | 1.7688 | 1.1162 | 0 | 19.665 | 12.533 | 8.0781 | 4.2273 | 6.5466 | 4.2888 | 2.7904 | 2.0953
122 | 508 | 25.5562 | 15.4212 | 8.4889 | 5.4648 | 3.5717 | 2.2561 | 1.7829 | 1.1251 | 0 | 19.8211 | 12.6325 | 8.1422 | 4.2609 | 6.5986 | 4.3229 | 2.8125 | 2.1119
123 | 513 | 25.8078 | 15.573 | 8.5724 | 5.5186 | 3.6069 | 2.2783 | 1.8004 | 1.1362 | 0 | 20.0162 | 12.7568 | 8.2224 | 4.3028 | 6.6635 | 4.3654 | 2.8402 | 2.1327
124 | 517 | 26.009 | 15.6944 | 8.6393 | 5.5616 | 3.635 | 2.2961 | 1.8145 | 1.145 | 0 | 20.1723 | 12.8563 | 8.2865 | 4.3364 | 6.7155 | 4.3995 | 2.8623 | 2.1494
125 | 521 | 26.2102 | 15.8159 | 8.7061 | 5.6046 | 3.6631 | 2.3139 | 1.8285 | 1.1539 | 0 | 20.3283 | 12.9557 | 8.3506 | 4.3699 | 6.7674 | 4.4335 | 2.8845 | 2.166
126 | 525 | 26.4114 | 15.9373 | 8.773 | 5.6476 | 3.6912 | 2.3316 | 1.8425 | 1.1627 | 0 | 20.4844 | 13.0552 | 8.4147 | 4.4035 | 6.8194 | 4.4675 | 2.9066 | 2.1826
127 | 529 | 26.6127 | 16.0587 | 8.8398 | 5.6907 | 3.7194 | 2.3494 | 1.8566 | 1.1716 | 0 | 20.6405 | 13.1547 | 8.4788 | 4.437 | 6.8713 | 4.5016 | 2.9288 | 2.1992
128 | 533 | 26.8139 | 16.1801 | 8.9066 | 5.7337 | 3.7475 | 2.3672 | 1.8706 | 1.1804 | 0 | 20.7966 | 13.2542 | 8.5429 | 4.4706 | 6.9233 | 4.5356 | 2.9509 | 2.2159
129 | 538 | 27.0654 | 16.3319 | 8.9902 | 5.7875 | 3.7826 | 2.3894 | 1.8882 | 1.1915 | 0 | 20.9916 | 13.3785 | 8.623 | 4.5125 | 6.9882 | 4.5782 | 2.9786 | 2.2367
130 | 542 | 27.2667 | 16.4533 | 9.057 | 5.8305 | 3.8108 | 2.4071 | 1.9022 | 1.2004 | 0 | 21.1477 | 13.478 | 8.6872 | 4.5461 | 7.0402 | 4.6122 | 3.0007 | 2.2533
131 | 546 | 27.4679 | 16.5748 | 9.1239 | 5.8735 | 3.8389 | 2.4249 | 1.9162 | 1.2092 | 0 | 21.3038 | 13.5774 | 8.7513 | 4.5796 | 7.0922 | 4.6462 | 3.0229 | 2.2699
132 | 550 | 27.6691 | 16.6962 | 9.1907 | 5.9166 | 3.867 | 2.4427 | 1.9303 | 1.2181 | 0 | 21.4599 | 13.6769 | 8.8154 | 4.6132 | 7.1441 | 4.6803 | 3.045 | 2.2865
133 | 554 | 27.8704 | 16.8176 | 9.2576 | 5.9596 | 3.8951 | 2.4604 | 1.9443 | 1.227 | 0 | 21.6159 | 13.7764 | 8.8795 | 4.6467 | 7.1961 | 4.7143 | 3.0672 | 2.3032
134 | 558 | 28.0716 | 16.9391 | 9.3244 | 6.0026 | 3.9233 | 2.4782 | 1.9583 | 1.2358 | 0 | 21.772 | 13.8758 | 8.9436 | 4.6803 | 7.248 | 4.7483 | 3.0893 | 2.3198
135 | 563 | 28.3231 | 17.0908 | 9.4079 | 6.0564 | 3.9584 | 2.5004 | 1.9759 | 1.2469 | 0 | 21.9671 | 14.0002 | 9.0237 | 4.7222 | 7.313 | 4.7909 | 3.117 | 2.3406
136 | 567 | 28.5244 | 17.2123 | 9.4748 | 6.0995 | 3.9865 | 2.5182 | 1.9899 | 1.2557 | 0 | 22.1232 | 14.0996 | 9.0879 | 4.7558 | 7.3649 | 4.8249 | 3.1391 | 2.3572
137 | 571 | 28.7256 | 17.3337 | 9.5416 | 6.1425 | 4.0147 | 2.5359 | 2.004 | 1.2646 | 0 | 22.2792 | 14.1991 | 9.152 | 4.7893 | 7.4169 | 4.859 | 3.1613 | 2.3738
138 | 575 | 28.9268 | 17.4551 | 9.6085 | 6.1855 | 4.0428 | 2.5537 | 2.018 | 1.2735 | 0 | 22.4353 | 14.2986 | 9.2161 | 4.8229 | 7.4688 | 4.893 | 3.1834 | 2.3905
139 | 579 | 29.1281 | 17.5765 | 9.6753 | 6.2285 | 4.0709 | 2.5715 | 2.0321 | 1.2823 | 0 | 22.5914 | 14.398 | 9.2802 | 4.8564 | 7.5208 | 4.927 | 3.2056 | 2.4071
140 | 583 | 29.3293 | 17.698 | 9.7422 | 6.2716 | 4.099 | 2.5892 | 2.0461 | 1.2912 | 0 | 22.7475 | 14.4975 | 9.3443 | 4.89 | 7.5728 | 4.9611 | 3.2277 | 2.4237
141 | 588 | 29.5808 | 17.8498 | 9.8257 | 6.3254 | 4.1342 | 2.6114 | 2.0636 | 1.3023 | 0 | 22.9425 | 14.6218 | 9.4244 | 4.9319 | 7.6377 | 5.0036 | 3.2554 | 2.4445
142 | 592 | 29.7821 | 17.9712 | 9.8925 | 6.3684 | 4.1623 | 2.6292 | 2.0777 | 1.3111 | 0 | 23.0986 | 14.7213 | 9.4886 | 4.9655 | 7.6897 | 5.0377 | 3.2776 | 2.4612
143 | 596 | 29.9833 | 18.0926 | 9.9594 | 6.4114 | 4.1904 | 2.647 | 2.0917 | 1.32 | 0 | 23.2547 | 14.8208 | 9.5527 | 4.999 | 7.7416 | 5.0717 | 3.2997 | 2.4778
144 | 600 | 30.1845 | 18.214 | 10.0262 | 6.4544 | 4.2186 | 2.6647 | 2.1058 | 1.3288 | 0 | 23.4108 | 14.9202 | 9.6168 | 5.0326 | 7.7936 | 5.1057 | 3.3218 | 2.4944
145 | 604 | 30.3857 | 18.3355 | 10.0931 | 6.4975 | 4.2467 | 2.6825 | 2.1198 | 1.3377 | 0 | 23.5668 | 15.0197 | 9.6809 | 5.0661 | 7.8455 | 5.1398 | 3.344 | 2.511
146 | 608 | 30.587 | 18.4569 | 10.1599 | 6.5405 | 4.2748 | 2.7003 | 2.1338 | 1.3466 | 0 | 23.7229 | 15.1192 | 9.745 | 5.0997 | 7.8975 | 5.1738 | 3.3661 | 2.5277
147 | 613 | 30.8385 | 18.6087 | 10.2435 | 6.5943 | 4.31 | 2.7225 | 2.1514 | 1.3576 | 0 | 23.918 | 15.2435 | 9.8251 | 5.1416 | 7.9624 | 5.2164 | 3.3938 | 2.5485
148 | 617 | 31.0397 | 18.7301 | 10.3103 | 6.6373 | 4.3381 | 2.7402 | 2.1654 | 1.3665 | 0 | 24.0741 | 15.343 | 9.8893 | 5.1751 | 8.0144 | 5.2504 | 3.416 | 2.5651
149 | 621 | 31.241 | 18.8515 | 10.3771 | 6.6804 | 4.3662 | 2.758 | 2.1795 | 1.3753 | 0 | 24.2301 | 15.4425 | 9.9534 | 5.2087 | 8.0664 | 5.2844 | 3.4381 | 2.5817
150 | 625 | 31.4422 | 18.973 | 10.444 | 6.7234 | 4.3943 | 2.7758 | 2.1935 | 1.3842 | 0 | 24.3862 | 15.5419 | 10.0175 | 5.2422 | 8.1183 | 5.3185 | 3.4603 | 2.5983
151 | 629 | 31.6434 | 19.0944 | 10.5108 | 6.7664 | 4.4225 | 2.7935 | 2.2075 | 1.3931 | 0 | 24.5423 | 15.6414 | 10.0816 | 5.2758 | 8.1703 | 5.3525 | 3.4824 | 2.615
152 | 633 | 31.8447 | 19.2158 | 10.5777 | 6.8094 | 4.4506 | 2.8113 | 2.2216 | 1.4019 | 0 | 24.6983 | 15.7409 | 10.1457 | 5.3093 | 8.2222 | 5.3866 | 3.5046 | 2.6316
153 | 638 | 32.0962 | 19.3676 | 10.6612 | 6.8632 | 4.4857 | 2.8335 | 2.2391 | 1.413 | 0 | 24.8934 | 15.8652 | 10.2258 | 5.3513 | 8.2872 | 5.4291 | 3.5322 | 2.6524
154 | 642 | 32.2974 | 19.489 | 10.7281 | 6.9063 | 4.5139 | 2.8513 | 2.2532 | 1.4219 | 0 | 25.0495 | 15.9647 | 10.29 | 5.3848 | 8.3391 | 5.4631 | 3.5544 | 2.669
155 | 646 | 32.4987 | 19.6104 | 10.7949 | 6.9493 | 4.542 | 2.869 | 2.2672 | 1.4307 | 0 | 25.2056 | 16.0641 | 10.3541 | 5.4184 | 8.3911 | 5.4972 | 3.5765 | 2.6857
156 | 650 | 32.6999 | 19.7319 | 10.8617 | 6.9923 | 4.5701 | 2.8868 | 2.2812 | 1.4396 | 0 | 25.3617 | 16.1636 | 10.4182 | 5.4519 | 8.443 | 5.5312 | 3.5987 | 2.7023
157 | 654 | 32.9011 | 19.8533 | 10.9286 | 7.0353 | 4.5982 | 2.9045 | 2.2953 | 1.4484 | 0 | 25.5177 | 16.2631 | 10.4823 | 5.4855 | 8.495 | 5.5653 | 3.6208 | 2.7189
158 | 658 | 33.1023 | 19.9747 | 10.9954 | 7.0784 | 4.6264 | 2.9223 | 2.3093 | 1.4573 | 0 | 25.6738 | 16.3625 | 10.5464 | 5.519 | 8.547 | 5.5993 | 3.643 | 2.7355
159 | 663 | 33.3539 | 20.1265 | 11.079 | 7.1322 | 4.6615 | 2.9445 | 2.3269 | 1.4684 | 0 | 25.8689 | 16.4869 | 10.6265 | 5.561 | 8.6119 | 5.6418 | 3.6706 | 2.7563
160 | 667 | 33.5551 | 20.2479 | 11.1458 | 7.1752 | 4.6896 | 2.9623 | 2.3409 | 1.4772 | 0 | 26.025 | 16.5863 | 10.6907 | 5.5945 | 8.6639 | 5.6759 | 3.6928 | 2.773
161 | 671 | 33.7563 | 20.3694 | 11.2127 | 7.2182 | 4.7178 | 2.9801 | 2.3549 | 1.4861 | 0 | 26.181 | 16.6858 | 10.7548 | 5.6281 | 8.7158 | 5.7099 | 3.7149 | 2.7896
162 | 675 | 33.9576 | 20.4908 | 11.2795 | 7.2613 | 4.7459 | 2.9978 | 2.369 | 1.4949 | 0 | 26.3371 | 16.7853 | 10.8189 | 5.6616 | 8.7678 | 5.744 | 3.7371 | 2.8062
163 | 679 | 34.1588 | 20.6122 | 11.3463 | 7.3043 | 4.774 | 3.0156 | 2.383 | 1.5038 | 0 | 26.4932 | 16.8847 | 10.883 | 5.6952 | 8.8197 | 5.778 | 3.7592 | 2.8228
164 | 683 | 34.36 | 20.7336 | 11.4132 | 7.3473 | 4.8021 | 3.0333 | 2.397 | 1.5127 | 0 | 26.6492 | 16.9842 | 10.9471 | 5.7287 | 8.8717 | 5.812 | 3.7814 | 2.8395
165 | 688 | 34.6116 | 20.8854 | 11.4967 | 7.4011 | 4.8373 | 3.0556 | 2.4146 | 1.5237 | 0 | 26.8443 | 17.1085 | 11.0272 | 5.7707 | 8.9366 | 5.8546 | 3.8091 | 2.8603
166 | 692 | 34.8128 | 21.0069 | 11.5636 | 7.4441 | 4.8654 | 3.0733 | 2.4286 | 1.5326 | 0 | 27.0004 | 17.208 | 11.0914 | 5.8042 | 8.9886 | 5.8886 | 3.8312 | 2.8769
167 | 696 | 35.014 | 21.1283 | 11.6304 | 7.4872 | 4.8935 | 3.0911 | 2.4427 | 1.5414 | 0 | 27.1565 | 17.3075 | 11.1555 | 5.8378 | 9.0406 | 5.9227 | 3.8533 | 2.8935
168 | 700 | 35.2153 | 21.2497 | 11.6973 | 7.5302 | 4.9217 | 3.1088 | 2.4567 | 1.5503 | 0 | 27.3126 | 17.407 | 11.2196 | 5.8713 | 9.0925 | 5.9567 | 3.8755 | 2.9101
169 | 704 | 35.4165 | 21.3711 | 11.7641 | 7.5732 | 4.9498 | 3.1266 | 2.4707 | 1.5592 | 0 | 27.4686 | 17.5064 | 11.2837 | 5.9049 | 9.1445 | 5.9907 | 3.8976 | 2.9268
170 | 708 | 35.6177 | 21.4926 | 11.831 | 7.6163 | 4.9779 | 3.1444 | 2.4848 | 1.568 | 0 | 27.6247 | 17.6059 | 11.3478 | 5.9384 | 9.1964 | 6.0248 | 3.9198 | 2.9434
171 | 713 | 35.8693 | 21.6443 | 11.9145 | 7.67 | 5.0131 | 3.1666 | 2.5023 | 1.5791 | 0 | 27.8198 | 17.7302 | 11.4279 | 5.9804 | 9.2614 | 6.0673 | 3.9475 | 2.9642
172 | 717 | 36.0705 | 21.7658 | 11.9813 | 7.7131 | 5.0412 | 3.1843 | 2.5164 | 1.588 | 0 | 27.9759 | 17.8297 | 11.4921 | 6.0139 | 9.3133 | 6.1014 | 3.9696 | 2.9808
173 | 721 | 36.2717 | 21.8872 | 12.0482 | 7.7561 | 5.0693 | 3.2021 | 2.5304 | 1.5968 | 0 | 28.1319 | 17.9292 | 11.5562 | 6.0475 | 9.3653 | 6.1354 | 3.9918 | 2.9975
174 | 725 | 36.473 | 22.0086 | 12.115 | 7.7991 | 5.0974 | 3.2199 | 2.5445 | 1.6057 | 0 | 28.288 | 18.0286 | 11.6203 | 6.081 | 9.4172 | 6.1694 | 4.0139 | 3.0141
175 | 729 | 36.6742 | 22.1301 | 12.1819 | 7.8422 | 5.1255 | 3.2376 | 2.5585 | 1.6145 | 0 | 28.4441 | 18.1281 | 11.6844 | 6.1146 | 9.4692 | 6.2035 | 4.036 | 3.0307
176 | 733 | 36.8754 | 22.2515 | 12.2487 | 7.8852 | 5.1537 | 3.2554 | 2.5725 | 1.6234 | 0 | 28.6001 | 18.2276 | 11.7485 | 6.1481 | 9.5212 | 6.2375 | 4.0582 | 3.0473
177 | 738 | 37.127 | 22.4033 | 12.3323 | 7.939 | 5.1888 | 3.2776 | 2.5901 | 1.6345 | 0 | 28.7952 | 18.3519 | 11.8286 | 6.19 | 9.5861 | 6.2801 | 4.0859 | 3.0681
178 | 742 | 37.3282 | 22.5247 | 12.3991 | 7.982 | 5.217 | 3.2954 | 2.6041 | 1.6433 | 0 | 28.9513 | 18.4514 | 11.8928 | 6.2236 | 9.6381 | 6.3141 | 4.108 | 3.0848
179 | 746 | 37.5294 | 22.6461 | 12.4659 | 8.025 | 5.2451 | 3.3131 | 2.6182 | 1.6522 | 0 | 29.1074 | 18.5508 | 11.9569 | 6.2571 | 9.69 | 6.3481 | 4.1302 | 3.1014
180 | 750 | 37.7306 | 22.7675 | 12.5328 | 8.0681 | 5.2732 | 3.3309 | 2.6322 | 1.661 | 0 | 29.2634 | 18.6503 | 12.021 | 6.2907 | 9.742 | 6.3822 | 4.1523 | 3.118
181 | 754 | 37.9319 | 22.889 | 12.5996 | 8.1111 | 5.3013 | 3.3487 | 2.6462 | 1.6699 | 0 | 29.4195 | 18.7498 | 12.0851 | 6.3242 | 9.7939 | 6.4162 | 4.1745 | 3.1346
182 | 758 | 38.1331 | 23.0104 | 12.6665 | 8.1541 | 5.3294 | 3.3664 | 2.6603 | 1.6788 | 0 | 29.5756 | 18.8492 | 12.1492 | 6.3578 | 9.8459 | 6.4503 | 4.1966 | 3.1513
183 | 763 | 38.3846 | 23.1622 | 12.75 | 8.2079 | 5.3646 | 3.3886 | 2.6778 | 1.6898 | 0 | 29.7707 | 18.9736 | 12.2293 | 6.3997 | 9.9108 | 6.4928 | 4.2243 | 3.1721
184 | 767 | 38.5859 | 23.2836 | 12.8169 | 8.2509 | 5.3927 | 3.4064 | 2.6919 | 1.6987 | 0 | 29.9268 | 19.073 | 12.2935 | 6.4333 | 9.9628 | 6.5268 | 4.2464 | 3.1887
185 | 771 | 38.7871 | 23.405 | 12.8837 | 8.294 | 5.4208 | 3.4242 | 2.7059 | 1.7076 | 0 | 30.0828 | 19.1725 | 12.3576 | 6.4668 | 10.0147 | 6.5609 | 4.2686 | 3.2053
186 | 775 | 38.9883 | 23.5265 | 12.9505 | 8.337 | 5.449 | 3.4419 | 2.7199 | 1.7164 | 0 | 30.2389 | 19.272 | 12.4217 | 6.5004 | 10.0667 | 6.5949 | 4.2907 | 3.222
187 | 779 | 39.1896 | 23.6479 | 13.0174 | 8.38 | 5.4771 | 3.4597 | 2.734 | 1.7253 | 0 | 30.395 | 19.3715 | 12.4858 | 6.5339 | 10.1187 | 6.629 | 4.3129 | 3.2386
188 | 783 | 39.3908 | 23.7693 | 13.0842 | 8.4231 | 5.5052 | 3.4775 | 2.748 | 1.7341 | 0 | 30.551 | 19.4709 | 12.5499 | 6.5675 | 10.1706 | 6.663 | 4.335 | 3.2552
189 | 788 | 39.6423 | 23.9211 | 13.1678 | 8.4768 | 5.5404 | 3.4997 | 2.7656 | 1.7452 | 0 | 30.7461 | 19.5953 | 12.63 | 6.6094 | 10.2356 | 6.7055 | 4.3627 | 3.276
190 | 792 | 39.8436 | 24.0425 | 13.2346 | 8.5199 | 5.5685 | 3.5174 | 2.7796 | 1.7541 | 0 | 30.9022 | 19.6947 | 12.6942 | 6.643 | 10.2875 | 6.7396 | 4.3848 | 3.2926
191 | 796 | 40.0448 | 24.164 | 13.3015 | 8.5629 | 5.5966 | 3.5352 | 2.7936 | 1.7629 | 0 | 31.0583 | 19.7942 | 12.7583 | 6.6765 | 10.3395 | 6.7736 | 4.407 | 3.3093
192 | 800 | 40.246 | 24.2854 | 13.3683 | 8.6059 | 5.6247 | 3.553 | 2.8077 | 1.7718 | 0 | 31.2143 | 19.8937 | 12.8224 | 6.7101 | 10.3914 | 6.8077 | 4.4291 | 3.3259
193 | 804 | 40.4472 | 24.4068 | 13.4351 | 8.649 | 5.6529 | 3.5707 | 2.8217 | 1.7806 | 0 | 31.3704 | 19.9931 | 12.8865 | 6.7436 | 10.4434 | 6.8417 | 4.4513 | 3.3425
194 | 808 | 40.6485 | 24.5282 | 13.502 | 8.692 | 5.681 | 3.5885 | 2.8357 | 1.7895 | 0 | 31.5265 | 20.0926 | 12.9506 | 6.7772 | 10.4954 | 6.8757 | 4.4734 | 3.3591
195 | 813 | 40.9 | 24.68 | 13.5855 | 8.7458 | 5.7161 | 3.6107 | 2.8533 | 1.8006 | 0 | 31.7216 | 20.2169 | 13.0307 | 6.8191 | 10.5603 | 6.9183 | 4.5011 | 3.3799
196 | 817 | 41.1012 | 24.8014 | 13.6524 | 8.7888 | 5.7443 | 3.6285 | 2.8673 | 1.8094 | 0 | 31.8776 | 20.3164 | 13.0949 | 6.8527 | 10.6123 | 6.9523 | 4.5233 | 3.3966
197 | 821 | 41.3025 | 24.9229 | 13.7192 | 8.8318 | 5.7724 | 3.6462 | 2.8814 | 1.8183 | 0 | 32.0337 | 20.4159 | 13.159 | 6.8862 | 10.6642 | 6.9864 | 4.5454 | 3.4132
198 | 825 | 41.5037 | 25.0443 | 13.7861 | 8.8749 | 5.8005 | 3.664 | 2.8954 | 1.8271 | 0 | 32.1898 | 20.5153 | 13.2231 | 6.9198 | 10.7162 | 7.0204 | 4.5675 | 3.4298
199 | 829 | 41.7049 | 25.1657 | 13.8529 | 8.9179 | 5.8286 | 3.6818 | 2.9094 | 1.836 | 0 | 32.3459 | 20.6148 | 13.2872 | 6.9533 | 10.7681 | 7.0544 | 4.5897 | 3.4464
200 | 833 | 41.9062 | 25.2872 | 13.9197 | 8.9609 | 5.8568 | 3.6995 | 2.9235 | 1.8449 | 0 | 32.5019 | 20.7143 | 13.3513 | 6.9869 | 10.8201 | 7.0885 | 4.6118 | 3.4631
201 | 838 | 42.1577 | 25.4389 | 14.0033 | 9.0147 | 5.8919 | 3.7217 | 2.941 | 1.8559 | 0 | 32.697 | 20.8386 | 13.4314 | 7.0288 | 10.885 | 7.131 | 4.6395 | 3.4839
202 | 842 | 42.3589 | 25.5604 | 14.0701 | 9.0577 | 5.92 | 3.7395 | 2.9551 | 1.8648 | 0 | 32.8531 | 20.9381 | 13.4956 | 7.0624 | 10.937 | 7.1651 | 4.6617 | 3.5005
203 | 846 | 42.5602 | 25.6818 | 14.137 | 9.1008 | 5.9482 | 3.7573 | 2.9691 | 1.8737 | 0 | 33.0092 | 21.0375 | 13.5597 | 7.0959 | 10.9889 | 7.1991 | 4.6838 | 3.5171
204 | 850 | 42.7614 | 25.8032 | 14.2038 | 9.1438 | 5.9763 | 3.775 | 2.9831 | 1.8825 | 0 | 33.1652 | 21.137 | 13.6238 | 7.1295 | 11.0409 | 7.2331 | 4.706 | 3.5338
205 | 854 | 42.9626 | 25.9246 | 14.2707 | 9.1868 | 6.0044 | 3.7928 | 2.9972 | 1.8914 | 0 | 33.3213 | 21.2365 | 13.6879 | 7.163 | 11.0929 | 7.2672 | 4.7281 | 3.5504
206 | 858 | 43.1639 | 26.0461 | 14.3375 | 9.2299 | 6.0325 | 3.8106 | 3.0112 | 1.9002 | 0 | 33.4774 | 21.336 | 13.752 | 7.1966 | 11.1448 | 7.3012 | 4.7502 | 3.567
207 | 863 | 43.4154 | 26.1979 | 14.4211 | 9.2836 | 6.0677 | 3.8328 | 3.0288 | 1.9113 | 0 | 33.6725 | 21.4603 | 13.8321 | 7.2385 | 11.2098 | 7.3438 | 4.7779 | 3.5878
208 | 867 | 43.6166 | 26.3193 | 14.4879 | 9.3267 | 6.0958 | 3.8505 | 3.0428 | 1.9202 | 0 | 33.8285 | 21.5598 | 13.8963 | 7.272 | 11.2617 | 7.3778 | 4.8001 | 3.6044
209 | 871 | 43.8179 | 26.4407 | 14.5547 | 9.3697 | 6.1239 | 3.8683 | 3.0569 | 1.929 | 0 | 33.9846 | 21.6592 | 13.9604 | 7.3056 | 11.3137 | 7.4118 | 4.8222 | 3.6211
210 | 875 | 44.0191 | 26.5621 | 14.6216 | 9.4127 | 6.1521 | 3.8861 | 3.0709 | 1.9379 | 0 | 34.1407 | 21.7587 | 14.0245 | 7.3391 | 11.3656 | 7.4459 | 4.8444 | 3.6377
211 | 879 | 44.2203 | 26.6836 | 14.6884 | 9.4558 | 6.1802 | 3.9038 | 3.0849 | 1.9467 | 0 | 34.2968 | 21.8582 | 14.0886 | 7.3727 | 11.4176 | 7.4799 | 4.8665 | 3.6543
212 | 883 | 44.4215 | 26.805 | 14.7553 | 9.4988 | 6.2083 | 3.9216 | 3.099 | 1.9556 | 0 | 34.4528 | 21.9576 | 14.1527 | 7.4062 | 11.4695 | 7.514 | 4.8887 | 3.6709
213 | 888 | 44.6731 | 26.9568 | 14.8388 | 9.5526 | 6.2435 | 3.9438 | 3.1165 | 1.9667 | 0 | 34.6479 | 22.082 | 14.2328 | 7.4482 | 11.5345 | 7.5565 | 4.9163 | 3.6917
214 | 892 | 44.8743 | 27.0782 | 14.9057 | 9.5956 | 6.2716 | 3.9616 | 3.1306 | 1.9755 | 0 | 34.804 | 22.1814 | 14.297 | 7.4817 | 11.5865 | 7.5905 | 4.9385 | 3.7084
215 | 896 | 45.0755 | 27.1996 | 14.9725 | 9.6386 | 6.2997 | 3.9793 | 3.1446 | 1.9844 | 0 | 34.9601 | 22.2809 | 14.3611 | 7.5153 | 11.6384 | 7.6246 | 4.9606 | 3.725
216 | 900 | 45.2768 | 27.3211 | 15.0393 | 9.6817 | 6.3278 | 3.9971 | 3.1586 | 1.9933 | 0 | 35.1161 | 22.3804 | 14.4252 | 7.5488 | 11.6904 | 7.6586 | 4.9828 | 3.7416
217 | 904 | 45.478 | 27.4425 | 15.1062 | 9.7247 | 6.356 | 4.0149 | 3.1727 | 2.0021 | 0 | 35.2722 | 22.4798 | 14.4893 | 7.5824 | 11.7423 | 7.6927 | 5.0049 | 3.7582
218 | 908 | 45.6792 | 27.5639 | 15.173 | 9.7677 | 6.3841 | 4.0326 | 3.1867 | 2.011 | 0 | 35.4283 | 22.5793 | 14.5534 | 7.6159 | 11.7943 | 7.7267 | 5.0271 | 3.7749
219 | 913 | 45.9308 | 27.7157 | 15.2566 | 9.8215 | 6.4192 | 4.0548 | 3.2043 | 2.022 | 0 | 35.6234 | 22.7036 | 14.6335 | 7.6579 | 11.8592 | 7.7692 | 5.0547 | 3.7957
220 | 917 | 46.132 | 27.8371 | 15.3234 | 9.8646 | 6.4474 | 4.0726 | 3.2183 | 2.0309 | 0 | 35.7794 | 22.8031 | 14.6977 | 7.6914 | 11.9112 | 7.8033 | 5.0769 | 3.8123
221 | 921 | 46.3332 | 27.9585 | 15.3903 | 9.9076 | 6.4755 | 4.0904 | 3.2323 | 2.0398 | 0 | 35.9355 | 22.9026 | 14.7618 | 7.725 | 11.9631 | 7.8373 | 5.099 | 3.8289
222 | 925 | 46.5345 | 28.08 | 15.4571 | 9.9506 | 6.5036 | 4.1081 | 3.2464 | 2.0486 | 0 | 36.0916 | 23.002 | 14.8259 | 7.7585 | 12.0151 | 7.8714 | 5.1212 | 3.8456
223 | 929 | 46.7357 | 28.2014 | 15.5239 | 9.9936 | 6.5317 | 4.1259 | 3.2604 | 2.0575 | 0 | 36.2477 | 23.1015 | 14.89 | 7.7921 | 12.0671 | 7.9054 | 5.1433 | 3.8622
224 | 933 | 46.9369 | 28.3228 | 15.5908 | 10.0367 | 6.5599 | 4.1436 | 3.2744 | 2.0663 | 0 | 36.4037 | 23.201 | 14.9541 | 7.8256 | 12.119 | 7.9394 | 5.1655 | 3.8788
225 | 938 | 47.1885 | 28.4746 | 15.6743 | 10.0905 | 6.595 | 4.1659 | 3.292 | 2.0774 | 0 | 36.5988 | 23.3253 | 15.0342 | 7.8676 | 12.184 | 7.982 | 5.1932 | 3.8996
226 | 942 | 47.3897 | 28.596 | 15.7412 | 10.1335 | 6.6231 | 4.1836 | 3.306 | 2.0863 | 0 | 36.7549 | 23.4248 | 15.0984 | 7.9011 | 12.2359 | 8.016 | 5.2153 | 3.9162
227 | 946 | 47.5909 | 28.7175 | 15.808 | 10.1765 | 6.6513 | 4.2014 | 3.3201 | 2.0951 | 0 | 36.911 | 23.5243 | 15.1625 | 7.9347 | 12.2879 | 8.0501 | 5.2374 | 3.9329
228 | 950 | 47.7921 | 28.8389 | 15.8749 | 10.2195 | 6.6794 | 4.2191 | 3.3341 | 2.104 | 0 | 37.067 | 23.6237 | 15.2266 | 7.9682 | 12.3398 | 8.0841 | 5.2596 | 3.9495
229 | 954 | 47.9934 | 28.9603 | 15.9417 | 10.2626 | 6.7075 | 4.2369 | 3.3481 | 2.1128 | 0 | 37.2231 | 23.7232 | 15.2907 | 8.0018 | 12.3918 | 8.1181 | 5.2817 | 3.9661
230 | 958 | 48.1946 | 29.0817 | 16.0085 | 10.3056 | 6.7356 | 4.2547 | 3.3622 | 2.1217 | 0 | 37.3792 | 23.8227 | 15.3548 | 8.0353 | 12.4437 | 8.1522 | 5.3039 | 3.9827
231 | 963 | 48.4461 | 29.2335 | 16.0921 | 10.3594 | 6.7708 | 4.2769 | 3.3797 | 2.1328 | 0 | 37.5743 | 23.947 | 15.4349 | 8.0772 | 12.5087 | 8.1947 | 5.3316 | 4.0035
232 | 967 | 48.6474 | 29.355 | 16.1589 | 10.4024 | 6.7989 | 4.2946 | 3.3938 | 2.1416 | 0 | 37.7303 | 24.0465 | 15.4991 | 8.1108 | 12.5607 | 8.2288 | 5.3537 | 4.0202
233 | 971 | 48.8486 | 29.4764 | 16.2258 | 10.4455 | 6.827 | 4.3124 | 3.4078 | 2.1505 | 0 | 37.8864 | 24.1459 | 15.5632 | 8.1444 | 12.6126 | 8.2628 | 5.3759 | 4.0368
234 | 975 | 49.0498 | 29.5978 | 16.2926 | 10.4885 | 6.8552 | 4.3302 | 3.4218 | 2.1594 | 0 | 38.0425 | 24.2454 | 15.6273 | 8.1779 | 12.6646 | 8.2968 | 5.398 | 4.0534
235 | 979 | 49.2511 | 29.7192 | 16.3595 | 10.5315 | 6.8833 | 4.3479 | 3.4359 | 2.1682 | 0 | 38.1986 | 24.3449 | 15.6914 | 8.2115 | 12.7165 | 8.3309 | 5.4201 | 4.0701
236 | 983 | 49.4523 | 29.8407 | 16.4263 | 10.5745 | 6.9114 | 4.3657 | 3.4499 | 2.1771 | 0 | 38.3546 | 24.4443 | 15.7555 | 8.245 | 12.7685 | 8.3649 | 5.4423 | 4.0867
237 | 988 | 49.7038 | 29.9924 | 16.5099 | 10.6283 | 6.9466 | 4.3879 | 3.4675 | 2.1881 | 0 | 38.5497 | 24.5687 | 15.8356 | 8.2869 | 12.8334 | 8.4075 | 5.47 | 4.1075
238 | 992 | 49.9051 | 30.1139 | 16.5767 | 10.6714 | 6.9747 | 4.4057 | 3.4815 | 2.197 | 0 | 38.7058 | 24.6681 | 15.8997 | 8.3205 | 12.8854 | 8.4415 | 5.4921 | 4.1241
239 | 996 | 50.1063 | 30.2353 | 16.6435 | 10.7144 | 7.0028 | 4.4234 | 3.4955 | 2.2059 | 0 | 38.8619 | 24.7676 | 15.9639 | 8.354 | 12.9373 | 8.4755 | 5.5143 | 4.1407
240 | 1000 | 50.3075 | 30.3567 | 16.7104 | 10.7574 | 7.0309 | 4.4412 | 3.5096 | 2.2147 | 0 | 39.0179 | 24.8671 | 16.028 | 8.3876 | 12.9893 | 8.5096 | 5.5364 | 4.1574
241 | 1004 | 50.5088 | 30.4782 | 16.7772 | 10.8004 | 7.0591 | 4.459 | 3.5236 | 2.2236 | 0 | 39.174 | 24.9665 | 16.0921 | 8.4211 | 13.0413 | 8.5436 | 5.5586 | 4.174
242 | 1008 | 50.71 | 30.5996 | 16.8441 | 10.8435 | 7.0872 | 4.4767 | 3.5377 | 2.2324 | 0 | 39.3301 | 25.066 | 16.1562 | 8.4547 | 13.0932 | 8.5777 | 5.5807 | 4.1906
243 | 1013 | 50.9615 | 30.7514 | 16.9276 | 10.8973 | 7.1223 | 4.4989 | 3.5552 | 2.2435 | 0 | 39.5252 | 25.1903 | 16.2363 | 8.4966 | 13.1582 | 8.6202 | 5.6084 | 4.2114
244 | 1017 | 51.1628 | 30.8728 | 16.9945 | 10.9403 | 7.1505 | 4.5167 | 3.5693 | 2.2524 | 0 | 39.6812 | 25.2898 | 16.3004 | 8.5302 | 13.2101 | 8.6542 | 5.6305 | 4.228
245 | 1021 | 51.364 | 30.9942 | 17.0613 | 10.9833 | 7.1786 | 4.5345 | 3.5833 | 2.2612 | 0 | 39.8373 | 25.3893 | 16.3646 | 8.5637 | 13.2621 | 8.6883 | 5.6527 | 4.2447

## Transformer Sizing Matrix (hidden)
| Summer | Winter
Load | Transformer | Transformer
1 | 10 | 10
2 | 10 | 10
3 | 10 | 10
4 | 10 | 10
5 | 10 | 10
6 | 10 | 10
7 | 10 | 10
8 | 10 | 10
9 | 10 | 10
10 | 10 | 10
11 | 10 | 10
12 | 15 | 15
13 | 15 | 15
14 | 15 | 15
15 | 15 | 15
16 | 15 | 15
17 | 15 | 15
18 | 25 | 15
19 | 25 | 25
20 | 25 | 25
21 | 25 | 25
22 | 25 | 25
23 | 25 | 25
24 | 25 | 25
25 | 25 | 25
26 | 25 | 25
27 | 25 | 25
28 | 25 | 25
29 | 37.5 | 25
30 | 37.5 | 25
31 | 37.5 | 37.5
32 | 37.5 | 37.5
33 | 37.5 | 37.5
34 | 37.5 | 37.5
35 | 37.5 | 37.5
36 | 37.5 | 37.5
37 | 37.5 | 37.5
38 | 37.5 | 37.5
39 | 37.5 | 37.5
40 | 37.5 | 37.5
41 | 37.5 | 37.5
42 | 37.5 | 37.5
43 | 50 | 37.5
44 | 50 | 37.5
45 | 50 | 37.5
46 | 50 | 50
47 | 50 | 50
48 | 50 | 50
49 | 50 | 50
50 | 50 | 50
51 | 50 | 50
52 | 50 | 50
53 | 50 | 50
54 | 50 | 50
55 | 50 | 50
56 | 75 | 50
57 | 75 | 50
58 | 75 | 50
59 | 75 | 50
60 | 75 | 50
61 | 75 | 75
62 | 75 | 75
63 | 75 | 75
64 | 75 | 75
65 | 75 | 75
66 | 75 | 75
67 | 75 | 75
68 | 75 | 75
69 | 75 | 75
70 | 75 | 75
71 | 75 | 75
72 | 75 | 75
73 | 75 | 75
74 | 75 | 75
75 | 75 | 75
76 | 75 | 75
77 | 75 | 75
78 | 75 | 75
79 | 75 | 75
80 | 75 | 75
81 | 75 | 75
82 | 75 | 75
83 | 75 | 75
84 | 100 | 75
85 | 100 | 75
86 | 100 | 75
87 | 100 | 75
88 | 100 | 75
89 | 100 | 75
90 | 100 | 75
91 | 100 | 100
92 | 100 | 100
93 | 100 | 100
94 | 100 | 100
95 | 100 | 100
96 | 100 | 100
97 | 100 | 100
98 | 100 | 100
99 | 100 | 100
100 | 100 | 100
101 | 100 | 100
102 | 100 | 100
103 | 100 | 100
104 | 100 | 100
105 | 100 | 100
106 | 100 | 100
107 | 100 | 100
108 | 100 | 100
109 | 100 | 100
110 | 100 | 100
111 | 167 | 100
112 | 167 | 100
113 | 167 | 100
114 | 167 | 100
115 | 167 | 100
116 | 167 | 100
117 | 167 | 100
118 | 167 | 100
119 | 167 | 100
120 | 167 | 100
121 | 167 | 167
122 | 167 | 167
123 | 167 | 167
124 | 167 | 167
125 | 167 | 167
126 | 167 | 167
127 | 167 | 167
128 | 167 | 167
129 | 167 | 167
130 | 167 | 167
131 | 167 | 167
132 | 167 | 167
133 | 167 | 167
134 | 167 | 167
135 | 167 | 167
136 | 167 | 167
137 | 167 | 167
138 | 167 | 167
139 | 167 | 167
140 | 167 | 167
141 | 167 | 167
142 | 167 | 167
143 | 167 | 167
144 | 167 | 167
145 | 167 | 167
146 | 167 | 167
147 | 167 | 167
148 | 167 | 167
149 | 167 | 167
150 | 167 | 167
151 | 167 | 167
152 | 167 | 167
153 | 167 | 167
154 | 167 | 167
155 | 167 | 167
156 | 167 | 167
157 | 167 | 167
158 | 167 | 167
159 | 167 | 167
160 | 167 | 167
161 | 167 | 167
162 | 167 | 167
163 | 167 | 167
164 | 167 | 167
165 | 167 | 167
166 | 167 | 167
167 | 167 | 167
168 | 167 | 167
169 | 167 | 167
170 | 167 | 167
171 | 167 | 167
172 | 167 | 167
173 | 167 | 167
174 | 167 | 167
175 | 167 | 167
176 | 167 | 167
177 | 167 | 167
178 | 167 | 167
179 | 167 | 167
180 | 167 | 167
181 | 167 | 167
182 | 167 | 167
183 | 167 | 167
184 | 167 | 167
185 |  | 167
186 |  | 167
187 |  | 167
188 |  | 167
189 |  | 167
190 |  | 167
191 |  | 167
192 |  | 167
193 |  | 167
194 |  | 167
195 |  | 167
196 |  | 167
197 |  | 167
198 |  | 167
199 |  | 167
200 |  | 167
201 |  | 167
202
203
204
205
206
207
208